## Worksheet 0
PdmarticleID#PdmarticleID | Label#Label | External Key#ExternalKey | Nominal voltage#83 | Power consumption in operation#67 | Power consumption in rest position#68 | Power consumption for wire sizing#69 | Connection#6759 | Nominal torque#260 | Spring torque value#117 | Actuating force#118 | Emergency control function#890 | Angle of rotation#473 | Running time motor#230 | Running time reference#3645 | Running time emergency control position#3474 | Sound power level motor#135 | Control#281 | Positioning signal Y#120 | Control signal Y variable#5695 | Operating range Y#121 | Position feedback U#122 | Connection supply / control#96 | Degree of protection IEC/EN#144 | Direction of motion motor#119 | Auxiliary switch#112 | Spindle driver#137 | Ambient temperature#156 | 6287 | Product picture 4c/bw#377 | Data sheet name#406 | Data sheet PDF#660 | Company [Competitor]#7687 | Serie Actuator [Competitor]#7606 | Product type Actuator [Competitor]#7614 | Voltage [Competitor]#7607 | Sound power level [Competitor]#7608 | Control type [Competitor]#7609 | Running Time min [Competitor]#7610 | Running Time max [Competitor]#7776 | Torque [Competitor]#7611 | Stroke [Competitor]#7612 | Power consumption [Competitor]#7681 | Connection [Competitor]#7682 | Safety function [Competitor]#7683 | Integrated switch [Competitor]#7684 | Integrated potentiometer [Competitor]#7685 | Degree of protection [Competitor]#7686 | Angle of rotation [Competitor]#7771 | Working range [Competitor]#7772 | Positioning feedback [Competitor]#7773 | Spindle driver [Competitor]#7774 | Manual override [Competitor]#7775 | Additional Specification [Competitor]#7613 | Belimo Retrofit1 Antrieb#7597 | Belimo Retrofit1 Accessory1#7604 | Belimo Retrofit1 Accessory2#7777 | Belimo Retrofit1 Actuator Note#7881 | Belimo Retrofit2 Actuator#7680 | Belimo Retrofit2 Accessory1#7697 | Belimo Retrofit2 Accessory2#7778 | Belimo Retrofit2 Actuator Note#7882 | Belimo Retrofit3 Actuator#7688 | Belimo Retrofit3 Accessory#7698 | Belimo Retrofit3 Actuator Note#7883 | Belimo Retrofit4 Actuator#7704 | Belimo Retrofit4 Accessory#7705 | Belimo Retrofit4 Actuator Note#7884 | Version Number#VersionNr | Path#Path
PdmarticleID | Label | ExternalKey | 83 | 67 | 68 | 69 | 6759 | 260 | 117 | 118 | 890 | 473 | 230 | 3645 | 3474 | 135 | 281 | 120 | 5695 | 121 | 122 | 96 | 144 | 119 | 112 | 137 | 156 | 6287 | 377 | 406 | 660 | 7687 | 7606 | 7614 | 7607 | 7608 | 7609 | 7610 | 7776 | 7611 | 7612 | 7681 | 7682 | 7683 | 7684 | 7685 | 7686 | 7771 | 7772 | 7773 | 7774 | 7775 | 7613 | 7597 | 7604 | 7777 | 7881 | 7680 | 7697 | 7778 | 7882 | 7688 | 7698 | 7883 | 7704 | 7705 | 7884 | VersionNr | Path
301718 | LM24/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 5 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301390 | N20010-SER-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | modulating | 95 s |  | 20 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° | DC 0...30 V / 0...60 mA adjustable | DC 0...10 V | 10...27 mm | gear disengagement |  | SM24A-MP-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
288488 | GEB136.2E | [30 empty] | Siemens | GEB | Luftklappen-Linearantriebe | AC 24 V |  | 3-point | 150 s |  |  | 400 N | 4 VA | 0.9 m |  | 2 x SPDT |  | IP40 | [20 empty] | 28 | EU\Competitors valves retrofit\Air solution\Siemens\
301877 | SM24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301555 | SAL2.23S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 125 s |  | 24 Nm |  | 3.6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM230A-TP | S2A |  | for 3-point control get in touch with your local Belimo support¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301879 | SM24 EK | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301552 | SAL1.23 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 125 s |  | 24 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM24A-TP |  |  |  | GM24A-MP-TP |  |  | for 3-point control, AC only¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301392 | N20230-2POS | [30 empty] | Honeywell |  |  | AC 230 V | 40 dB(A) | Open-close | 110 s |  | 20 Nm |  | 8 VA | Terminal |  |  |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement |  | SM230A-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
288492 | GEB166.2E | [30 empty] | Siemens | GEB | Luftklappen-Linearantriebe | AC 24 V |  | modulating | 150 s |  |  | 400 N | 6 VA | 0.9 m |  | 2 x SPDT |  | IP40 | [20 empty] | 26 | EU\Competitors valves retrofit\Air solution\Siemens\
304325 | SFP-512-3 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF230-S |  |  |  | LF230 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
301881 | SM24 NC | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301554 | SAL2.23 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 125 s |  | 24 Nm |  | 3.6 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM230A-TP |  |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
288486 | GEB132.2E | [30 empty] | Siemens | GEB | Luftklappen-Linearantriebe | AC 24 V |  | 3-point | 150 s |  |  | 400 N | 4 VA | 0.9 m |  |  |  | IP40 | [5 empty] | Poti 1 kOhm | [14 empty] | 26 | EU\Competitors valves retrofit\Air solution\Siemens\
301394 | N20230-SW2 | [30 empty] | Honeywell |  |  | AC 230 V | 40 dB(A) | 3-point | 110 s |  | 20 Nm |  | 8 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement |  | SM230A-S-TP |  |  |  | SM230A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301717 | LM24/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 3 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301715 | LM24 HG | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 113 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Belimo\
301719 | LM24-5P0 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  | 5 kΩ | 6...16 mm |  |  | LM24AP5 | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301391 | N20230 | [30 empty] | Honeywell |  |  | AC 230 V | 40 dB(A) | 3-point | 110 s |  | 20 Nm |  | 8 VA | Terminal |  |  |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement |  | SM230A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301556 | SAS1.23 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 30 s |  | 8 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NMC24A-MP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
288490 | GEB161.2E | [30 empty] | Siemens | GEB |  | AC 24 V |  | modulating | 150 s |  |  | 400 N | 6 VA | 0.9 m |  |  |  | IP40 | [6 empty] | SH24A-MP100 |  |  |  | SH24A-SR100 | [9 empty] | 26 | EU\Competitors valves retrofit\Air solution\Siemens\
301878 | SM24 BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301880 | SM24 H | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301389 | N20010-SER | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | modulating | 95 s |  | 20 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° | DC 0...30 V / 0...60 mA adjustable | DC 0...10 V | 10...27 mm | gear disengagement |  | SM24A-MP-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
288494 | GEB331.2E | [30 empty] | Siemens | GEB | Luftklappen-Linearantriebe | AC 230 V |  | 3-point | 150 s |  |  | 400 N | 3 VA | 0.9 m |  |  |  | IP40 | [6 empty] | SH230A100 | [13 empty] | 26 | EU\Competitors valves retrofit\Air solution\Siemens\
301553 | SAL1.23S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 125 s |  | 24 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | GM24A-MP-TP | S2A |  | for 3-point control, AC only¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301393 | N20230-P10K | [30 empty] | Honeywell |  |  | AC 230 V | 40 dB(A) | 3-point | 110 s |  | 20 Nm |  | 8 VA | Terminal |  |  |  | IP54 | 95° |  | 10 kΩ | 10...27 mm | gear disengagement |  | SM230A-TP | P10000A | [12 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301716 | LM24 RE | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301551 | SA2.23S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 80 s |  | 16 Nm |  | 3.6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SM230A-S-TP |  |  |  | SM230A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301876 | SM230/300 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 80 s | 150 s | 15 Nm |  | 17 VA | 3 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304324 | SFP-512-2 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF230-S |  |  |  | LF230 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
288484 | GEB131.2E | [30 empty] | Siemens | GEB | Luftklappen-Linearantriebe | AC 24 V |  | 3-point | 150 s |  |  | 400 N | 4 VA | 0.9 m |  |  |  | IP40 | [6 empty] | SH24A100 | [13 empty] | 27 | EU\Competitors valves retrofit\Air solution\Siemens\
301714 | LM24 H | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 112 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Belimo\
301723 | LM24-F BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 111 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-F | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Belimo\
301403 | S10230-2POS | [30 empty] | Honeywell |  |  | AC 230 V | 50 dB(A) | Open-close | 45 s |  | 10 Nm |  | 45 VA |  | yes |  |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | NFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301882 | SM24 RT | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301400 | N3424 | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | 3-point | 110 s |  | 34 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement |  | GM24A-MP-TP |  |  | for 3-point control, AC only¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301567 | SM4.2S | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
298075 | ML6184E1017 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | 3-point | 110 s |  | 17 Nm |  | 6 VA | 1 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 10...16 mm | gear disengagement |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Honeywell\
301731 | LM24-FS-T | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | Terminal |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-S-TP |  |  |  | LM24A-F | S1A | [8 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
288498 | GEB336.2E | [30 empty] | Siemens | GEB | Luftklappen-Linearantriebe | AC 230 V |  | 3-point | 150 s |  |  | 400 N | 3 VA | 0.9 m |  | 2 x SPDT |  | IP40 | [20 empty] | 27 | EU\Competitors valves retrofit\Air solution\Siemens\
301560 | SM1.10 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 16 s |  | 16 Nm |  | 15 VA | Terminal |  |  |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | SMQ24A-SR |  |  | for 0…20 mA use an external 500 Ω resistor¦ | SMQ24A-MF |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301890 | SM24-SR H | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  |  | SM24A-PC | Z-SMA | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301395 | N2024 | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | 3-point | 110 s |  | 20 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement |  | SM24A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301887 | SM240 BL | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 17 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301726 | LM24-F-5P0-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° |  | 5 kΩ | 8 mm |  |  | LM24A-F | P5000A |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304340 | ASF122F122 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 6.4...20 mm | gear disengagement |  | SF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Sauter\
304333 | ASF112F120 | [30 empty] | Sauter |  |  | AC 230 V |  | Open-close | 90 s |  | 7 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | NFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Sauter\
301397 | N2024-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | 3-point | 110 s |  | 20 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement |  | SM24A-S-TP |  |  |  | SM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
298077 | N2024-P10K | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | 3-point | 110 s |  | 20 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° |  | 10 kΩ | 10...27 mm | gear disengagement |  | SM24A-TP | P10000A | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Honeywell\
301720 | LM24-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
298074 | 238-230-15-S2 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 150 s |  | 15 Nm |  | 8 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 100° |  |  | 9...20 mm | hand crank |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Gruner\
298072 | SM24-S H | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close | 20 s |  | 15 Nm |  | 5 VA | 0.9 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 10...20 mm |  |  | SMQ24A | S1A | Z-SMA | [11 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
301405 | S1024-2POS | [30 empty] | Honeywell |  |  | AC 24 V | 50 dB(A) | Open-close | 45 s |  | 10 Nm |  | 30 VA |  | yes |  |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | NF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301728 | LM24-FS-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m (halogen-free) |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-S |  |  | Connection: cable 1 m, PVC¦ | LM24A-F | S1A |  | Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301884 | SM24/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 3 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301564 | SM1.23 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 60 s |  | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | SMC24A-MP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | SM24A-MP-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301569 | SM4.5S | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301557 | SAS1.23S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 30 s |  | 8 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NMC24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301562 | SM1.12 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 8 s |  | 8 Nm |  | 15 VA | Terminal |  |  |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | NMQ24A-SR |  |  | for 0…20 mA use an external 500 Ω resistor¦ | NMQ24A-MF |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301399 | N34230 | [30 empty] | Honeywell |  |  | AC 230 V | 40 dB(A) | 3-point | 110 s |  | 34 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement | [15 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301722 | LM24-F | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301566 | SM4.2 | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301892 | SM24-SR RT | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  |  | SM24A-PC | Z-SMA | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301402 | S10010-SW2 | [30 empty] | Honeywell |  |  | AC/DC 24 V | 40 dB(A) | modulating | 90 s |  | 10 Nm |  | 14 VA |  | yes | 2 x SPDT |  | IP54 | 95° | DC 0(2)...10 V |  | 10...27 mm | hand crank |  | NF24A-SR-S2 |  |  |  | NF24A-SR | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
304342 | ASF122F222 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 6.4...20 mm | gear disengagement |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
301725 | LM24-F-5P0 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  | 5 kΩ | 8 mm |  |  | LM24A-F | P5000A | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301886 | SM240 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 17 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301559 | SAS2.23S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 30 s |  | 8 Nm |  | 3.6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NM230A-S-TP |  |  |  | NM230A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304339 | ASF122F120 | [30 empty] | Sauter |  |  | AC 230 V |  | Open-close | 90 s |  | 18 Nm |  | 8 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 6.4...20 mm | gear disengagement |  | SFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Sauter\
288496 | GEB332.2E | [30 empty] | Siemens | GEB | Luftklappen-Linearantriebe | AC 230 V |  | 3-point | 150 s |  |  | 400 N | 3 VA | 0.9 m |  |  |  | IP40 | [5 empty] | Poti 1 kOhm | [14 empty] | 26 | EU\Competitors valves retrofit\Air solution\Siemens\
304337 | ASF113F122 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | 3-point | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | NF24A-3 | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
298079 | DM1.1FSK | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | modulating | 90 s |  | 16 Nm |  | 12 VA | 1 m (halogen-free) | yes | 2 x SPDT |  | IP54 | 93° | DC 0...10 V | DC 0...10 V | 10...20 mm | hand crank |  | SF24A-SZ-S2 |  |  | Connection: cable 1 m, PVC¦ | SF24A-SZ | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | [6 empty] | 39 | EU\Competitors valves retrofit\Air solution\Joventa\
301894 | SM24-SR/500 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 5 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  | Connection: cable 1 m, PVC¦ | SM24A-PC | Z-SMA |  | Connection: cable 1 m, PVC¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304335 | ASF112F220 | [30 empty] | Sauter |  |  | AC 230 V |  | Open-close | 90 s |  | 7 Nm |  | 7 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
301724 | LM24-F/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301404 | S10230-2POS-SW2 | [30 empty] | Honeywell |  |  | AC 230 V | 50 dB(A) | Open-close | 45 s |  | 10 Nm |  | 45 VA |  | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301396 | N2024-2POS | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | Open-close | 110 s |  | 20 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° |  |  | 10...27 mm | gear disengagement |  | SM24A-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301407 | S20010 | [30 empty] | Honeywell |  |  | AC/DC 24 V | 40 dB(A) | modulating | 90 s |  | 20 Nm |  | 16 VA |  | yes |  |  | IP54 | 95° | DC 0(2)...10 V |  | 10...27 mm | hand crank |  | SF24A-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Honeywell\
301730 | LM24-FS-C7/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 5 m (halogen-free) |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-S |  |  | Connection: cable 1 m, PVC¦ | LM24A-F | S1A |  | Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301889 | SM24-SR BL | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  |  | SM24A-PC | Z-SMA | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301401 | S10010 | [30 empty] | Honeywell |  |  | AC/DC 24 V | 40 dB(A) | modulating | 90 s |  | 10 Nm |  | 14 VA |  | yes |  |  | IP54 | 95° | DC 0(2)...10 V |  | 10...27 mm | hand crank |  | NF24A-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Honeywell\
301561 | SM1.10S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 16 s |  | 16 Nm |  | 15 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | SMQ24A-SR | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | SMQ24A-MF | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
298068 | AM230 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 39 | EU\Competitors valves retrofit\Air solution\Belimo\
301891 | SM24-SR HG | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  |  | SM24A-PC | Z-SMA | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301883 | SM24 SW | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301732 | LM24-F-T | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | Terminal |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-TP |  |  |  | LM24A-F | [9 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301568 | SM4.5 | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301563 | SM1.12S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 8 s |  | 8 Nm |  | 15 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | NMQ24A-SR | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | NMQ24A-MF | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301398 | N34010 | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | modulating | 95 s |  | 34 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...27 mm | gear disengagement |  | GM24A-SR-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | GM24A-MP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
298076 | N20010-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | modulating | 95 s |  | 20 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...27 mm | gear disengagement |  | SM24A-SR-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | SM24A-MP-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Honeywell\
298073 | BEP-10F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | NF24A-MP |  |  | for 3-point control, AC only¦ | NF24A-3 |  |  |  | NF24G-MP-L |  | for 3-point control, AC only¦ |  |  |  | 42 | EU\Competitors valves retrofit\Air solution\Elodrive\
298078 | M9116-GGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | modulating | 80 s | 110 s | 16 Nm |  | 7.5 VA |  |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm |  |  | SM24A-SR | [13 empty] | 36 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301721 | LM24-C7/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 3 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
298081 | GEB136.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 15 Nm |  | 4 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | SM24A-S |  |  |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 26 | EU\Competitors valves retrofit\Air solution\Siemens\
301885 | SM24/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 4 VA | 5 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301888 | SM24-SR | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  |  | SM24A-PC | Z-SMA | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304341 | ASF122F220 | [30 empty] | Sauter |  |  | AC 230 V |  | Open-close | 90 s |  | 18 Nm |  | 8 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 6.4...20 mm | gear disengagement |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
301727 | LM24-FS | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-S |  |  |  | LM24A-F | S1A | [8 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
304334 | ASF112F122 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | NF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Sauter\
301729 | LM24-FS-C7/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 3 m (halogen-free) |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LM24A-S |  |  | Connection: cable 1 m, PVC¦ | LM24A-F | S1A |  | Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301558 | SAS2.23 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 30 s |  | 8 Nm |  | 3.6 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NM230A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301570 | SML1.23 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 125 s |  | 24 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | GM24A-SR-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | GM24A-MP-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304336 | ASF112F222 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
301406 | S1024-2POS-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 50 dB(A) | Open-close | 45 s |  | 10 Nm |  | 30 VA |  | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301565 | SM1.23S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 60 s |  | 16 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | SMC24A-MP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | SM24A-MP-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301408 | S20010-SW2 | [30 empty] | Honeywell |  |  | AC/DC 24 V | 40 dB(A) | modulating | 90 s |  | 20 Nm |  | 16 VA |  | yes | 2 x SPDT |  | IP54 | 95° | DC 0(2)...10 V |  | 10...27 mm | hand crank |  | SF24A-SR-S2 |  |  |  | SF24A-SR | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
304338 | ASF113SF122 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | modulating | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 6.4...20 mm | gear disengagement |  | NF24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
301893 | SM24-SR/300 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  | Connection: cable 1 m, PVC¦ | SM24A-PC | Z-SMA |  | Connection: cable 1 m, PVC¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301418 | M9108-GGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | modulating | 30 s | 45 s | 8 Nm |  | 7.5 VA |  |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm |  |  | NM24A-SR | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301572 | SML4.2 | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304343 | ASF123F122 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | 3-point | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 6.4...20 mm | gear disengagement |  | SF24A-3 | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
301416 | M9108-AGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6.5 VA |  |  |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | NMC24A-MP |  |  |  | NM24A | [9 empty] | 34 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301257 | BE-15D2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 3-wire | SFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301736 | LM24-S BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A-S | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304348 | ASF12F020(+HK1+HK2) | [30 empty] | Sauter |  |  | AC/DC 24 V |  | Open-close | 80 s |  | 12 Nm |  |  | 1 m | yes | 2 x SPDT |  | IP54 | 95° | [5 empty] | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
301577 | SMS1.23S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 30 s |  | 8 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | NMC24A-MP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301410 | S20230-2POS-SW2 | [30 empty] | Honeywell |  |  | AC 230 V | 50 dB(A) | Open-close | 45 s |  | 20 Nm |  | 60 VA |  | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301895 | SM24-SR/C76 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA |  |  | SM24A-PC | Z-SMA | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301249 | BE-10D2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 3-wire | NFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301254 | BE-15A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 2-wire | SF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301413 | M9106-AGC-2 | [30 empty] | Johnson Controls |  |  | AC 24 V |  | 3-point | 72 s |  | 6 Nm |  | 2.5 VA |  |  | 2 x SPDT |  | IP32 | 95° |  |  | 10...12.7 mm |  |  | LM24A-S |  |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301902 | SML24-SR | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 170 s | 300 s | 15 Nm |  |  | 0.9 m |  |  |  | IP54 | 96° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304355 | ASM114SF132 (SUT) | [30 empty] | Sauter |  |  | AC 24 V |  | multifunctional |  |  | 10 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 8...16 mm |  |  | NMC24A-MP |  |  |  | NM24A-MP |  |  |  | NM24A-SR | [5 empty] | 20 | EU\Competitors valves retrofit\Air solution\Sauter\
301743 | LM24-SR RE | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304345 | ASF12F001 | [30 empty] | Sauter |  |  | AC 230 V |  | Open-close | 80 s |  | 12 Nm |  |  | 1 m | yes |  |  | IP54 | 95° | [5 empty] | SFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Sauter\
301733 | LM24-J6 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | RJ11 |  |  |  | IP54 | 95° |  | 10 kΩ | 6...16 mm |  |  | LM24A | P10000A |  | Connection: cable 1 m, PVC¦ | LM24A-TP | P10000A |  | Connection: cable 1 m, PVC¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301574 | SML4.5 | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301579 | SMS4.2S | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304350 | ASM104F120 | [30 empty] | Sauter |  |  | AC 230 V | 30 dB(A) | 3-point | 120 s |  | 5 Nm |  | 1.6 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...16 mm |  |  | LM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
301738 | LM24-S-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m (halogen-free) |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A-S |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301420 | M9116-ADA-1 | [30 empty] | Johnson Controls |  |  | AC 230 V |  | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6 VA |  |  |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | SM230A | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301256 | BE-15D1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 3-wire | SF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301897 | SM24-SRS | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V |  | 10...20 mm |  |  | SM24A-MP | Z-SMA |  |  | SM24A-SR | Z-SMA | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301246 | BE-10A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 2-wire | NF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301899 | SMC220/500 | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 45 s |  | 10 Nm |  |  | 5 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SMD230A | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301581 | SMS4.5S | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301251 | BE-10F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301740 | LM24-SR BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304352 | ASM104SF132 (SUT) | [30 empty] | Sauter |  |  | AC 24 V |  | multifunctional |  |  | 5 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 8...16 mm |  |  | LMC24A-SR |  |  |  | LM24A-MP | [9 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
301248 | BE-10D1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 3-wire | NF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
304193 | FM12 F | [30 empty] | Belimo |  |  | AC/DC 24 V |  | Open-close | 150 s | 360 s | 5 Nm |  |  |  | yes | [9 empty] | NF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
301571 | SML1.23S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 125 s |  | 24 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | GM24A-SR-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | GM24A-MP-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301735 | LM24-S | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A-S | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304354 | ASM114F122 | [30 empty] | Sauter |  |  | AC 24 V | 30 dB(A) | 3-point | 120 s |  | 10 Nm |  | 1.5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...16 mm |  |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
304347 | ASF12F020 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | Open-close | 80 s |  | 12 Nm |  |  | 1 m | yes |  |  | IP54 | 95° | [5 empty] | SF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Sauter\
301745 | LM24-SR/300 BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304190 | DC-SM220 | [30 empty] | Belimo | [21 empty] | SM230A | Z-SMA | [12 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
301415 | M9108-ADA-1 | [30 empty] | Johnson Controls |  |  | AC 230 V |  | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6 VA |  |  |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | NM230A | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301576 | SMS1.23 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 30 s |  | 8 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...20 mm | gear disengagement |  | NMC24A-MP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301573 | SML4.2S | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301419 | M9108-HGA-2 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | modulating | 25 s | 50 s | 8 Nm |  | 6.5 VA |  |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm |  |  | NM24A-MP | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301409 | S20230-2POS | [30 empty] | Honeywell |  |  | AC 230 V | 50 dB(A) | Open-close | 45 s |  | 20 Nm |  | 60 VA |  | yes |  |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | SFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301412 | S2024-2POS-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 50 dB(A) | Open-close | 45 s |  | 20 Nm |  | 40 VA |  | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301901 | SMD24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 65 dB(A) | 2- / 3-point | 15 s | 20 s | 15 Nm |  | 15 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SMD24A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301417 | M9108-AGD-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6.5 VA |  |  |  |  | IP40 | 93° |  | 140 Ω | 10...20 mm |  |  | NMC24A-MP | P140A |  |  | NM24A | P140A | [8 empty] | 34 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301253 | BE-10P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301584 | AF230-S | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 11 VA | 1 m | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SFA-S2 | Z-SF |  |  | BF230-RE |  |  | fire protection¦ | [6 empty] | 40 | EU\Competitors valves retrofit\Air solution\Belimo\
304346 | ASF12F001(+HK1+HK2) | [30 empty] | Sauter |  |  | AC 230 V |  | Open-close | 80 s |  | 12 Nm |  |  | 1 m | yes | 2 x SPDT |  | IP54 | 95° | [5 empty] | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Sauter\
304344 | ASF123SF122 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | modulating | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 6.4...20 mm | gear disengagement |  | SF24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
301737 | LM24-S/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 5 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A-S |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304349 | ASF12SF001 | [30 empty] | Sauter |  |  | AC/DC 24 V |  | modulating | 80 s |  | 12 Nm |  |  | 1 m | yes |  |  | IP54 | 95° | DC 2...10 V |  |  |  |  | SF24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
301578 | SMS4.2 | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301742 | LM24-SR HG | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301258 | BE-15F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | SF24A-MP |  |  | for 3-point control, AC only¦ | SF24A-3 | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301744 | LM24-SR/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301411 | S2024-2POS | [30 empty] | Honeywell |  |  | AC 24 V | 50 dB(A) | Open-close | 45 s |  | 20 Nm |  | 40 VA |  | yes |  |  | IP54 | 95° |  |  | 10...27 mm | hand crank |  | SF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301896 | SM24-SRP | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 2...10V from L&G Polygyr RWF.. or positioner 0…1000 Ω (Brigde R/M removed) | DC 0.5...9.5 V | 10...20 mm | [16 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301250 | BE-10F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | NF24A-MP |  |  | for 3-point control, AC only¦ | NF24A-3 | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301414 | M9106-GGA-2 | [30 empty] | Johnson Controls |  |  | AC 24 V |  | modulating | 72 s |  | 6 Nm |  | 3.2 VA |  |  |  |  | IP32 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 10...12.7 mm |  |  | LM24A-SR | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301903 | SML24-SR BL | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 170 s | 300 s | 15 Nm |  |  | 0.9 m |  |  |  | IP54 | 97° | DC 2...10 V | DC 2...10 V | 10...20 mm |  |  | SM24A-SR | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301255 | BE-15A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 2-wire | SFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301421 | M9116-AGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA |  |  |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | SM24A | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301898 | SMC220 | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 45 s |  | 10 Nm |  |  | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SMD230A | Z-SMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301583 | AF230 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 11 VA | 1 m | yes |  |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SFA | Z-SF |  |  | BF230-RE |  |  | fire protection¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301247 | BE-10A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | 2-wire | NFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301575 | SML4.5S | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301739 | LM24-SR | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304351 | ASM104F122 | [30 empty] | Sauter |  |  | AC 24 V | 30 dB(A) | 3-point | 120 s |  | 5 Nm |  | 1.5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...16 mm |  |  | LM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
301580 | SMS4.5 | [30 empty] | Joventa |  |  | AC 110 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304356 | ASM124F130 | [30 empty] | Sauter |  |  | AC 230 V | 30 dB(A) | 3-point | 60/120 s |  | 15 Nm |  | 5.5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
301900 | SMC24 | [30 empty] | Belimo |  |  | AC 24 V |  | 2- / 3-point | 45 s | 85 s | 10 Nm |  |  | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SMC24A-MP | Z-SMA |  | for 3-point control, AC only¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301252 | BE-10P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | NF24A-MP | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301734 | LM24-MFT2 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | multifunctional | 75 s | 300 s | 4 Nm | [6 empty] | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A-MP | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301741 | LM24-SR H | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304353 | ASM114F120 | [30 empty] | Sauter |  |  | AC 230 V | 30 dB(A) | 3-point | 120 s |  | 10 Nm |  | 1.6 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...16 mm |  |  | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
304194 | FM12 F-R | [30 empty] | Belimo |  |  | AC/DC 24 V |  | Open-close | 150 s | 360 s | 5 Nm |  |  | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm |  |  | NF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
301588 | AF24-MFT2 | [30 empty] | Belimo |  |  | AC/DC 24 V | 48 dB(A) | multifunctional | <150 s |  | 15 Nm |  |  | 1 m | yes |  |  | IP57 | 95° |  |  | 10...20 mm | hand crank |  | SF24A-MP | Z-SF | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301433 | M9216-BDA-1 | [30 empty] | Johnson Controls |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 13 VA |  | yes |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | SFA | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301751 | LM24-SR-F BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | LM24A-SR-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301269 | BEP-15A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 2-wire | SF24A |  |  |  | SF24G-MP-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301585 | AF24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 10 VA | 1 m | yes |  |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SF24A | Z-SF |  |  | BF24-RE |  |  | fire protection¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301593 | AFR230-S | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 11 VA | 1 m | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SFA-S2 | Z-SF |  |  | SFA | S2A-F | Z-SF | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
301423 | M9116-AGC-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA |  |  | 2 x SPDT |  | IP40 | 93° |  |  | 10...20 mm |  |  | SM24A-S |  |  |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
304363 | GBB136.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 25 Nm |  | 7 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...25 mm | gear disengagement |  | GM24A-MP | S2A |  | for 3-point control, AC only¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304198 | FM12 FS-R | [30 empty] | Belimo |  |  | AC/DC 24 V |  | Open-close | 150 s | 360 s | 5 Nm |  |  | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm |  |  | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Belimo\
301264 | BEP-10D1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 3-wire | NF24A |  |  |  | NF24G-MP-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301746 | LM24-SR/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 5 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301756 | LM24-S-T | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | Terminal |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A-S-TP | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304365 | GBB163.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 25 Nm |  | 8 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...25 mm | gear disengagement |  | GM24A-MP | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304358 | ASM124SF132 (SUT) | [30 empty] | Sauter |  |  | AC 24 V |  | multifunctional |  |  | 15 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SMC24A-MP |  |  |  | SM24A-MP |  |  |  | SM24A-SR | [5 empty] | 20 | EU\Competitors valves retrofit\Air solution\Sauter\
304201 | FM6 F-L | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 80 s |  | 5 Nm |  |  | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm |  |  | NFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
304360 | ASM134SF132 (SUT) | [30 empty] | Sauter |  |  | AC 24 V |  | multifunctional |  |  | 30 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | GM24A-MP |  |  |  | GM24A-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Sauter\
301590 | AF24-SR | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | modulating | <150 s |  | 15 Nm |  | 10 VA | 1 m | yes |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm | hand crank |  | SF24A-SR | Z-SF | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301259 | BE-15F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301271 | BEP-15D1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 3-wire | SF24A |  |  |  | SF24G-MP-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301595 | AFR24-S | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 10 VA | 1 m | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SF24A-S2 | Z-SF |  |  | SF24A | S2A-F | Z-SF | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
301748 | LM24-SR-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301430 | M9206-BGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V | 55 dB(A) | Open-close | 10 s | 40 s | 6 Nm |  | 9.8 VA |  | yes |  |  | IP42 | 93° |  |  | 10...20 mm |  |  | NF24A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301425 | M9116-AGD-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA |  |  |  |  | IP40 | 93° |  | 140 Ω | 10...20 mm |  |  | SM24A | P140A | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301753 | LM24-SR-F/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | LM24A-SR-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301422 | M9116-AGA-2 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA |  |  |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | SM24A | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301427 | M9116-HGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | modulating | 80 s | 110 s | 16 Nm |  | 7.5 VA |  |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm |  |  | SM24A-MP | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301597 | AM110 | [30 empty] | Belimo |  |  | AC 110 V |  | Open-close | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304367 | GBB166.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 25 Nm |  | 8 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...25 mm | gear disengagement |  | GM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | GM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301750 | LM24-SR-F | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | LM24A-SR-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301261 | BE-15P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301266 | BEP-10F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304203 | FM6 FS-L | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 80 s |  | 5 Nm |  |  | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm |  |  | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Belimo\
304200 | FM6 FS | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 80 s |  | 5 Nm |  |  |  | yes | 2 x SPDT | [8 empty] | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Belimo\
304195 | FM12 FS | [30 empty] | Belimo |  |  | AC/DC 24 V |  | Open-close | 150 s | 360 s | 5 Nm |  |  |  | yes | 2 x SPDT | [8 empty] | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Belimo\
301758 | LM48 | [30 empty] | Belimo |  |  | DC 48 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  |  | 1 m |  |  |  | IP55 | 95° |  |  | 6...16 mm |  |  | LM72A | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301263 | BEP-10A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 2-wire | NFA |  |  |  | NFG-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301432 | M9206-GGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V | 55 dB(A) | modulating | 10 s | 40 s | 6 Nm |  | 9.8 VA |  | yes |  |  | IP42 | 93° | DC 0(2)...10 V | DC 0...10 V | 10...20 mm |  |  | NF24A-SR |  |  |  | NF24A-SZ | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301587 | AF24-MFT | [30 empty] | Belimo |  |  | AC/DC 24 V | 47 dB(A) | multifunctional | <150 s |  | 15 Nm |  |  | 1 m | yes |  |  | IP56 | 95° |  |  | 10...20 mm | hand crank |  | SF24A-MP | Z-SF | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301592 | AFR230 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 11 VA | 1 m | yes |  |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SFA | Z-SF | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301755 | LM24-SR-T-C2 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | Terminal |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 9 mm |  |  | LM24A-SR-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304362 | GBB135.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 25 Nm |  | 7 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  | 1 kΩ | 8...25 mm | gear disengagement |  | GM24A-MP | S2A |  | for 3-point control, AC only¦ accessory S2A with 2 adjustable switching points¦ | GM24A-MP | P1000A |  | for 3-point control, AC only¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304357 | ASM124F132 | [30 empty] | Sauter |  |  | AC 24 V | 30 dB(A) | 3-point | 60/120 s |  | 15 Nm |  | 5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
304369 | GBB335.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 25 Nm |  | 5 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  | 1 kΩ | 8...25 mm | gear disengagement | [15 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301589 | AF24-S | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 10 VA | 1 m | yes | 2 x SPDT |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SF24A-S2 | Z-SF |  |  | BF24-RE |  |  | fire protection¦ | [6 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
304205 | SMD24R | [30 empty] | Belimo |  |  | AC/DC 24 V | 65 dB(A) | 2- / 3-point | 15 s | 20 s | 15 Nm |  | 15 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SMD24A | Z-SMA | [12 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
304197 | FM12 FS-L | [30 empty] | Belimo |  |  | AC/DC 24 V |  | Open-close | 150 s | 360 s | 5 Nm |  |  | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm |  |  | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Belimo\
304364 | GBB161.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 25 Nm |  | 8 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...25 mm | gear disengagement |  | GM24A-MP |  |  |  | GM24A-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301268 | BEP-10P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301752 | LM24-SR-F HG | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | LM24A-SR-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301747 | LM24-SR-C104 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304199 | FM6 F | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 80 s |  | 5 Nm |  |  |  | yes | [9 empty] | NFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
301434 | M9216-BGA-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 18 VA |  | yes |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | SF24A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301270 | BEP-15A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 2-wire | SFA |  |  |  | SFG-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301429 | M9132-GGA-2 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | modulating | 115 s | 205 s | 32 Nm |  | 7.5 VA |  |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm |  |  | GM24A-SR | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301424 | M9116-AGC-2 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA |  |  | 2 x SPDT |  | IP40 | 93° |  |  | 10...20 mm |  |  | SM24A-S |  |  |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301594 | AFR24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close | <150 s |  | 15 Nm |  | 10 VA | 1 m | yes |  |  | IP54 | 95° |  |  | 10...20 mm | hand crank |  | SF24A | Z-SF | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301265 | BEP-10D2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 3-wire | NFA |  |  |  | NFG-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301586 | AF24LON | [30 empty] | Belimo |  |  | AC/DC 24 V | 46 dB(A) | LonWorks | <150 s |  | 15 Nm |  |  | 1 m | yes |  |  | IP55 | 95° |  |  | 10...20 mm | hand crank |  | SF24ALON | Z-SF | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301426 | M9116-GGA-2 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | modulating | 80 s | 110 s | 16 Nm |  | 7.5 VA |  |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm |  |  | SM24A-SR | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
304202 | FM6 F-R | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 80 s |  | 5 Nm |  |  | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm |  |  | NFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
301596 | AFR24-SR | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | modulating | <150 s |  | 15 Nm |  | 10 VA | 1 m | yes |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm | hand crank |  | SF24A-SR | Z-SF | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304366 | GBB164.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 25 Nm |  | 8 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...25 mm | gear disengagement |  | GM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304359 | ASM134F130 | [30 empty] | Sauter |  |  | AC 230 V | 30 dB(A) | 3-point | 120/240 s |  | 30 Nm |  | 4.7 VA | 1 m |  |  |  | IP54 | 95° |  |  | 10...20 mm | [16 empty] | 16 | EU\Competitors valves retrofit\Air solution\Sauter\
301591 | AF24-SR-S | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | modulating | <150 s |  | 15 Nm |  | 10 VA | 1 m | yes | 2 x SPDT |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 10...20 mm | hand crank |  | SF24A-SR-S2 | Z-SF |  |  | SF24A-SR | S2A-F | Z-SF | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301260 | BE-15P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | SF24A-MP | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304361 | GBB131.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 25 Nm |  | 7 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...25 mm | gear disengagement |  | GM24A-MP |  |  | for 3-point control, AC only¦ | [10 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301272 | BEP-15D2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 3-wire | SFA |  |  |  | SFG-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301754 | LM24-SR-F-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | LM24A-SR-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301757 | LM24-T | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | Terminal |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A-TP | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301431 | M9206-BGC-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V | 55 dB(A) | Open-close | 10 s | 40 s | 6 Nm |  | 9.8 VA |  | yes | 2 x SPDT |  | IP42 | 93° |  |  | 10...20 mm |  |  | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301428 | M9132-AGA-2 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V |  | 2- / 3-point | 115 s | 205 s | 32 Nm |  | 7.5 VA |  |  |  |  | IP40 | 93° |  |  | 10...20 mm |  |  | GM24A |  |  |  | GM24A-MP |  |  | for 3-point control, AC only¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301749 | LM24-SR-C7/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  | 4 VA | 5 m (halogen-free) |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM24A-SR |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304196 | FM12 F-L | [30 empty] | Belimo |  |  | AC/DC 24 V |  | Open-close | 150 s | 360 s | 5 Nm |  |  | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm |  |  | NF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Belimo\
301759 | LM48-SR | [30 empty] | Belimo |  |  | DC 48 V | 35 dB(A) | modulating | 80 s | 110 s | 4 Nm |  |  | 1 m |  |  |  | IP56 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LM72A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301267 | BEP-10P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | NF24A-MP |  |  |  | NF24G-MP-L | [9 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
304368 | GBB331.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 25 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...25 mm | gear disengagement | [15 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304204 | FM6 FS-R | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 80 s |  | 5 Nm |  |  | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm |  |  | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Belimo\
301262 | BEP-10A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 10 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | 2-wire | NF24A |  |  |  | NF24G-MP-L | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
304370 | GBB336.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 25 Nm |  | 5 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...25 mm | gear disengagement | [15 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301274 | BEP-15F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304377 | GCA164.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° | DC 0...10 V adjustable | DC 0...10 V | 8...25.6 mm | hand crank | piggyback | SF24A-MP | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | SF24A-SZ | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301610 | AM230-2-S | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S | Z-SMA |  |  | SM230A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
304380 | GCA326.1E | [30 empty] | Siemens |  |  | AC 230 V |  | Open-close | 90 s |  | 18 Nm |  | 8 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 8...25.6 mm | hand crank | piggyback | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
301440 | DA1.4FP1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA |  | yes |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | hand crank |  | SF24A-3 | P1000A |  |  | SF24A-MP | P1000A |  | for 3-point control, AC only¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
304216 | SQB21+ASC | [30 empty] | Landis&Gyr |  |  | AC 230 V |  | Open-close | 80 s |  | 12 Nm |  |  | 1 m | yes | 1 x SPDT |  | IP54 | 90° |  |  | 10...20 mm | hand crank |  | SFA-S2 | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301762 | LMC230/300 BL | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 3 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LMC230A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301435 | M9216-BGC-1 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 18 VA |  | yes | 2 x SPDT |  | IP40 | 93° |  |  | 10...20 mm |  |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301764 | LMC230-F | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC230A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301766 | LMC230-F-C5 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC230A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304372 | GCA126.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 8...25.6 mm | hand crank | piggyback | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
301443 | DA1.4FP2K | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA | 1 m (halogen-free) | yes |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | hand crank |  | SF24A-3 | P140A |  | Connection: cable 1 m, PVC¦ | SF24A-MP | P140A |  | for 3-point control, AC only¦ Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Joventa\
301282 | BN-10P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 10 Nm |  | 4 VA | 0.9 m |  |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm |  |  | NM24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301771 | LMC24-5P0 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  | 5 kΩ | 6...16 mm |  |  | LMC24A | P5000A | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301603 | AM230-2 BL | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301276 | BEP-15P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301279 | BN-05P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 5 Nm |  | 3 VA | 0.9 m |  |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm |  |  | LM24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301768 | LMC230-FS/300 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 3 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LMC230A-F | S1A |  | Connection: cable 1 m, PVC¦ | [10 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301437 | DA1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SM24A-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304218 | SQB61.1 | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | modulating | 80 s |  | 12 Nm |  | 25 VA | 1 m | yes |  |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 10...20 mm | hand crank | piggyback | SF24A-SR |  |  |  | SF24A-SZ | [9 empty] | 16 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
304382 | GDB132.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  | 1 kΩ | 8...16 mm | gear disengagement |  | LM24A | P1000A | [12 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301598 | AM110-2 | [30 empty] | Belimo |  |  | AC 110 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304374 | GCA135.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | 3-point | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° |  | 1 kΩ | 8...25.6 mm | hand crank | piggyback | SF24A-3 | P1000A-F | [12 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
301605 | AM230-2 H | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304379 | GCA321.1E | [30 empty] | Siemens |  |  | AC 230 V |  | Open-close | 90 s |  | 18 Nm |  | 8 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 8...25.6 mm | hand crank | piggyback | SFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301600 | AM230 BL | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301445 | DA1.4FSK | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA | 1 m (halogen-free) | yes | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A-3 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | SF24A-MP | S2A-F |  | for 3-point control, AC only¦ accessory S2A-F with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | [6 empty] | 41 | EU\Competitors valves retrofit\Air solution\Joventa\
301284 | BN-15C2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 2- / 3-point | 90 s |  | 15 Nm |  | 9 VA | 0.9 m |  |  |  | IP55 | 95° |  |  | 8...20 mm |  |  | SM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301439 | DA1.4FK | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA | 1 m (halogen-free) | yes |  |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A-3 |  |  | Connection: cable 1 m, PVC¦ | SF24A-MP |  |  | for 3-point control, AC only¦ Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Joventa\
301273 | BEP-15F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | SF24A-MP |  |  | for 3-point control, AC only¦ | SF24A-3 |  |  |  | SF24G-MP-L |  | for 3-point control, AC only¦ |  |  |  | 34 | EU\Competitors valves retrofit\Air solution\Elodrive\
301607 | AM230-2 RS | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301278 | BN-05C2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 2- / 3-point | 90 s |  | 5 Nm |  | 5 VA | 0.9 m |  |  |  | IP55 | 95° |  |  | 8...20 mm |  |  | LM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
304215 | SQB21.1+ASC1.8 | [30 empty] | Landis&Gyr |  |  | AC 230 V |  | Open-close | 80 s |  | 12 Nm |  | 25 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm | hand crank |  | SFA-S2 | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301770 | LMC24 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LMC24A | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304220 | SQB71.1 | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | Open-close | 80 s |  | 12 Nm |  | 25 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm | hand crank | piggyback | SF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301763 | LMC230/500 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 5 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LMC230A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301281 | BN-10C2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 2- / 3-point | 90 s |  | 10 Nm |  | 7 VA | 0.9 m |  |  |  | IP55 | 95° |  |  | 8...20 mm |  |  | NM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301760 | LMC100-F | [30 empty] | Belimo |  |  | AC 110 V | 45 dB(A) | Open-close | 25 s | 35 s | 3 Nm |  | 7 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC230A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304376 | GCA163.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° | DC 0...10 V adjustable | DC 0...10 V | 8...25.6 mm | hand crank | piggyback | SF24A-MP |  |  |  | SF24A-SZ | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301442 | DA1.4FP2 | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA |  | yes |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | hand crank |  | SF24A-3 | P140A |  |  | SF24A-MP | P140A |  | for 3-point control, AC only¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
301761 | LMC230 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LMC230A | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301609 | AM230-2 SW | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301447 | DA1.FK | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 18 VA | 1 m (halogen-free) | yes |  |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301602 | AM230-2 | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304217 | SQB61 | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | modulating | 80 s |  | 12 Nm |  |  | 1 m | yes |  |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 10...20 mm | hand crank |  | SF24A-SR |  |  |  | SF24A-SZ | [9 empty] | 16 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
304378 | GCA166.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 8...25.6 mm | hand crank | piggyback | SF24A-SZ-S2 |  |  |  | SF24A-SZ | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301765 | LMC230-F/300 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC230A-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304371 | GCA121.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 8...25.6 mm | hand crank | piggyback | SF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301275 | BEP-15P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 15 Nm |  | 20 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | SF24A-MP |  |  |  | SF24G-MP-L | [9 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
304381 | GDB131.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | LM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301611 | AM230-2-S BL | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S | Z-SMA |  |  | SM230A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301436 | M9216-GGA-2 | [30 empty] | Johnson Controls |  |  | AC/DC 24 V | 50 dB(A) | modulating | 90 s | 120 s | 16 Nm |  | 14 VA |  | yes |  |  | IP42 | 93° | DC 0(2)...10 V | DC 0...10 V | 10...20 mm |  |  | SF24A-SR |  |  |  | SF24A-SZ | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Johnson Controls\
301767 | LMC230-F-C89 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC230A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304214 | SQB21.1 | [30 empty] | Landis&Gyr |  |  | AC 230 V |  | Open-close | 80 s |  | 12 Nm |  | 25 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm | hand crank | piggyback | SFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301444 | DA1.4FS | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA |  | yes | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A-3 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | SF24A-MP | S2A-F |  | for 3-point control, AC only¦ accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Joventa\
304373 | GCA131.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | 3-point | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 8...25.6 mm | hand crank | piggyback | SF24A-3 | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
301283 | BN-15C1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 90 s |  | 15 Nm |  | 5.5 VA | 0.9 m |  |  |  | IP55 | 95° |  |  | 8...20 mm |  |  | SM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301277 | BN-05C1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 90 s |  | 5 Nm |  | 3 VA | 0.9 m |  |  |  | IP55 | 95° |  |  | 8...20 mm |  |  | LM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301772 | LMC24-F | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC24A-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301280 | BN-10C1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 90 s |  | 10 Nm |  | 4 VA | 0.9 m |  |  |  | IP55 | 95° |  |  | 8...20 mm |  |  | NM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301604 | AM230-2 ERE | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301769 | LMC230-S | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 25 s | 35 s | 3 Nm |  | 15 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LMC230A | S1A | [12 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301438 | DA1.4F | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA |  | yes |  |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A-3 |  |  |  | SF24A-MP |  |  | for 3-point control, AC only¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Joventa\
304375 | GCA161.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 18 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 8...25.6 mm | hand crank | piggyback | SF24A-SZ | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304219 | SQB71 | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | Open-close | 80 s |  | 12 Nm |  |  | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm | hand crank |  | SF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301606 | AM230-2 MAS | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304383 | GDB136.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | LM24A-S |  |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301599 | AM110-S | [30 empty] | Belimo |  |  | AC 110 V |  | Open-close | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S | Z-SMA |  |  | SM230A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301441 | DA1.4FP1K | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | 3-point | 90 s | 120 s | 16 Nm |  | 18 VA | 1 m (halogen-free) | yes |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | hand crank |  | SF24A-3 | P1000A |  | Connection: cable 1 m, PVC¦ | SF24A-MP | P1000A |  | for 3-point control, AC only¦ Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Joventa\
301608 | AM230-2 RT | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301601 | AM230 SW | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301446 | DA1.F | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 18 VA | Terminal | yes |  |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304221 | SQB71.1+ASC1.8 | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | Open-close | 80 s |  | 12 Nm |  | 25 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm | hand crank |  | SF24A-S2 | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301294 | BSP-04A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 4 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | LF230 | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
304223 | SQE35.12 | [30 empty] | Landis&Gyr |  |  | AC 230 V |  | 3-point | 150 s |  | 6 Nm | [13 empty] | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301285 | BN-15P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 15 Nm |  | 5.5 VA | 0.9 m |  |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm |  |  | SM24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301623 | AM24 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301777 | LMC24-S | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LMC24A | S1A | [12 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
304387 | GDB166.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 5 Nm |  | 3 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | LM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | LM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304393 | GEB161.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 15 Nm |  | 6 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 6.4...20 mm | gear disengagement | selfadaption | SM24A-MP |  |  |  | SM24A-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301779 | LMC24-SR-C104 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 25 s | 35 s | 3 Nm |  | 4.5 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LMC24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301620 | AM230-SR BL | [30 empty] | Belimo |  |  | AC 230 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM230ASR | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301287 | BS-04A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 4 Nm |  | 4.5 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | LF24 | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301448 | DA1.FS | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 18 VA | Terminal | yes | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301615 | AM230-2-T | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  | Terminal |  |  |  | IP54 | [6 empty] | SM230A-TP | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304233 | RCM-212 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  |  | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301453 | DA2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SM230A-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301458 | DA2.FK | [30 empty] | Joventa |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 13 VA | 1 m (halogen-free) | yes |  |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SFA |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304228 | SQR35.1 | [30 empty] | Landis&Gyr |  |  | AC 230 V |  | 3-point | 150 s |  | 15 Nm |  | 3 VA | Terminal |  |  |  | IP54 | 90° |  |  | 6...20 mm |  |  | SM230A-TP | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301781 | LMC24-SR-F-C104 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 25 s | 35 s | 3 Nm |  | 4.5 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | LMC24A-SR-F | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301774 | LMC24-F/500 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 5 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC24A-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301612 | AM230-2-S H | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S | Z-SMA |  |  | SM230A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
304395 | GEB164.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 15 Nm |  | 6 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 6.4...20 mm | gear disengagement | selfadaption | SM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301296 | BSP-04F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 90 s |  | 4 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301617 | AM230-S | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S | Z-SMA |  |  | SM230A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
304225 | SQE65.32 | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | modulating |  |  | 6 Nm | [8 empty] | DC 0...10 V |  |  |  |  | NM24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
304390 | GDB336.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | LM230A-S |  |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304230 | SQR65.18 | [30 empty] | Landis&Gyr |  |  | AC 24 V | 35 dB(A) | modulating | 150 s |  | 15 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 90° | DC 0...10 V |  | 6...20 mm |  |  | SM24A-MP-TP |  |  |  | SM24A-SR-TP | [9 empty] | 16 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301450 | DA1.P1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | SM24A-TP | P1000A | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304384 | GDB161.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 5 Nm |  | 3 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | LM24A-MP |  |  |  | LM24A-SR | [9 empty] | 19 | EU\Competitors valves retrofit\Air solution\Siemens\
304389 | GDB332.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  | 1 kΩ | 8...16 mm | gear disengagement |  | LM230A | P1000A | [12 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301460 | DA2.FSK | [30 empty] | Joventa |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 15 VA | 1 m (halogen-free) | yes | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SFA-S2 |  |  | Connection: cable 1 m, PVC¦ | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Joventa\
301783 | M24-5 | [30 empty] | Belimo |  |  | AC 24 V |  | 3-point | 240 s |  | 15 Nm |  | 2.1 VA |  |  |  |  | IP40 | 95° |  |  | 10...18 mm | gear disengagement |  | SM24A-MP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301455 | DA2.P2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | SM230A-TP | P140A | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301289 | BS-04F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 90 s |  | 4 Nm |  | 4.5 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | LF24-3 | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304392 | GEB132.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  | 1 kΩ | 6.4...20 mm | gear disengagement |  | SM24A | P1000A | [12 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301614 | AM230-2-S-T | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  | Terminal |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S-TP | Z-SMA |  |  | SM230A-TP | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
304222 | SQB71+ASC | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | Open-close | 80 s |  | 12 Nm |  | 25 VA | 1 m | yes | 1 x SPDT |  | IP54 | 90° |  |  | 10...20 mm | hand crank |  | SF24A-S2 | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301622 | AM230-T | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm |  |  | Terminal |  |  |  | IP54 | [6 empty] | SM230A-TP | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304227 | SQE85+ASC | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | 3-point |  |  | 6 Nm |  |  |  |  | 1 x SPDT | [8 empty] | NM24A-S | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301457 | DA2.F | [30 empty] | Joventa |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 13 VA | Terminal | yes |  |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SFA | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301298 | BSP-04P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 90 s |  | 4 Nm |  | 7 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301293 | BSP-04A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 90 s |  | 4 Nm |  | 4.5 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | LF24 | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301776 | LMC24-FS | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LMC24A-F | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301295 | BSP-04F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 90 s |  | 4 Nm |  | 4.5 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | LF24-3 | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301291 | BS-04P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 4 Nm |  | 4.5 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | LF24-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304232 | RCM-210 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | LM24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301286 | BN-15P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 90 s |  | 15 Nm |  | 8 VA | 0.9 m |  |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm |  |  | SM230ASR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301624 | AM24 BL | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304386 | GDB164.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 5 Nm |  | 3 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | LM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301780 | LMC24-SR-F | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 25 s | 35 s | 3 Nm |  | 4.5 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | LMC24A-SR-F | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301452 | DA1.S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SM24A-S-TP |  |  |  | SM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301621 | AM230-S-T | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm |  |  | Terminal |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S-TP | Z-SMA |  |  | SM230A-TP | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
304394 | GEB163.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 15 Nm |  | 6 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 6.4...20 mm | gear disengagement | selfadaption | SM24A-MP | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301785 | NM230 BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301778 | LMC24-SR | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 25 s | 35 s | 3 Nm |  | 4.5 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 6...16 mm |  |  | LMC24A-SR | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301619 | AM230-SR | [30 empty] | Belimo |  |  | AC 230 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM230ASR | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301773 | LMC24-F/300 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC24A-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304224 | SQE35+ASC | [30 empty] | Landis&Gyr |  |  | AC 230 V |  | 3-point |  |  | 6 Nm |  |  |  |  | 1 x SPDT | [8 empty] | NM230A-S | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301616 | AM230-C102 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM230A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301782 | M220-5 | [30 empty] | Belimo |  |  | AC 230 V |  | 3-point | 240 s |  | 15 Nm |  | 12 VA |  |  |  |  | IP40 | 95° |  |  | 10...18 mm | gear disengagement |  | SM230A | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301459 | DA2.FS | [30 empty] | Joventa |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 14 VA | Terminal | yes | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304234 | RCM-220 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 10 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | NM24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301454 | DA2.P1 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | SM230A-TP | P1000A | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304229 | SQR65.1 | [30 empty] | Landis&Gyr |  |  | AC 24 V | 35 dB(A) | modulating | 150 s |  | 15 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 90° | DC 0...10 V |  | 6...20 mm |  |  | SM24A-SR-TP | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301775 | LMC24-F-C89 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 25 s | 35 s | 3 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LMC24A-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301449 | DA1.FSK | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | Open-close | 90 s | 120 s | 16 Nm |  | 18 VA | 1 m (halogen-free) | yes | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | hand crank |  | SF24A-S2 |  |  | Connection: cable 1 m, PVC¦ | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Joventa\
304388 | GDB331.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | LM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304231 | SQR 85.1 | [30 empty] | Landis&Gyr |  |  | AC 24 V | 35 dB(A) | 3-point | 150 s |  | 15 Nm |  | 3 VA | Terminal |  |  |  | IP54 | 90° |  |  | 6...20 mm |  |  | SM24A-TP | [13 empty] | 18 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301297 | BSP-04P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 90 s |  | 4 Nm |  | 4.5 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | LF24-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304396 | GEB166.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 15 Nm |  | 6 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 6.4...20 mm | gear disengagement | selfadaption | SM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | SM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301618 | AM230-S/300 | [30 empty] | Belimo |  |  | AC 230 V |  | Open-close | 100 s | 150 s | 18 Nm |  |  | 3 m |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S | Z-SMA |  | Connection: cable 1 m, PVC¦ | SM230A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | [6 empty] | 39 | EU\Competitors valves retrofit\Air solution\Belimo\
304391 | GEB131.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 15 Nm |  | 4 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | SM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304226 | SQE85.12 | [30 empty] | Landis&Gyr |  |  | AC 24 V |  | 3-point | 150 s |  | 6 Nm | [13 empty] | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Landis & Gyr\
301288 | BS-04A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 90 s |  | 4 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | LF230 | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301613 | AM230-2-S/300 | [30 empty] | Belimo |  |  | AC 230 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  | 3 m |  | 2 x SPDT |  | IP54 | [6 empty] | SM230A-S | Z-SMA |  | Connection: cable 1 m, PVC¦ | SM230A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301784 | NM230 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301292 | BS-04P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 90 s |  | 4 Nm |  | 7 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301461 | DAB1.4 | [30 empty] | Joventa |  |  | AC 24 V | 35 dB(A) | 3-point | 35 s |  | 2 Nm |  | 1.8 W | 1.2 m (halogen-free) |  |  |  | IP42 | 93° |  |  | 8...13 mm | gear disengagement |  | TMC24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301456 | DA2.S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° |  |  | 10...20 mm | gear disengagement |  | SM230A-S-TP |  |  |  | SM230A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301451 | DA1.P2 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 80 s | 110 s | 16 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | SM24A-TP | P140A | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301290 | BS-04F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 90 s |  | 4 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304385 | GDB163.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 5 Nm |  | 3 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | LM24A-MP | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304408 | GIB335.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 35 Nm |  | 5 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  | 1 kΩ | 8...25 mm | no | [15 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301299 | BT-04A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 30 s |  | 4 Nm |  | 6 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | LF24 | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Elodrive\
304238 | RCM-510 | [30 empty] | Newenta |  |  | AC 100...230 V |  | modulating |  |  | 5 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | LM230ASR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
304398 | GEB332.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 15 Nm |  | 3 VA | 0.9 m |  |  |  | IP54 | 95° |  | 1 kΩ | 6.4...20 mm | gear disengagement |  | SM230A | P1000A | [12 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301630 | AM24-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  | 1 m (halogen-free) |  |  |  | IP54 | [6 empty] | SM24A | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304403 | GIB161.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 35 Nm |  | 8 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...25 mm | no |  | GM24A-MP |  |  |  | GM24A-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301635 | AM24-MFT2-T | [30 empty] | Belimo |  |  | AC/DC 24 V |  | multifunctional | 75 s | 300 s | 18 Nm |  |  | Terminal |  |  |  | IP55 | [6 empty] | SM24A-MP | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301307 | BTP-04F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 30 s |  | 4 Nm |  | 6 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | LF24-MFT |  |  |  | LF24-3 | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
301625 | AM24 H | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301473 | DAG2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 4.5 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM230A-TP |  |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301304 | BT-04P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 30 s |  | 4 Nm |  | 9.5 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301463 | DAD1.4 | [30 empty] | Joventa |  |  | AC 24 V | 35 dB(A) | 3-point | 72 s |  | 4 Nm |  | 2.2 W | 1.2 m (halogen-free) |  |  |  | IP42 | 93° |  |  | 8...13 mm | gear disengagement |  | LM24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301468 | DAF2.06S | [30 empty] | Joventa |  |  | AC 230 V | 55 dB(A) | Open-close | 10 s | 40 s | 6 Nm |  | 11 VA | 1.2 m (halogen-free) | yes | 1 x SPDT |  | IP54 | 93° |  |  | 10...16 mm |  |  | NFA-S2 |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
301789 | NM230/300 BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304245 | RCP-210 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301794 | NM230-2/300 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301786 | NM230 H | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301637 | AM24-S BL | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM24A-S | Z-SMA |  |  | SM24A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301301 | BT-04F1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | 3-point | 30 s |  | 4 Nm |  | 6 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | LF24-MFT |  |  |  | LF24-3 | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Elodrive\
304240 | RCM-530 | [30 empty] | Newenta |  |  | AC 100...230 V |  | modulating |  |  | 15 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | SM230ASR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301306 | BTP-04A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 30 s |  | 4 Nm |  | 9 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | LF230 | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301309 | BTP-04P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 30 s |  | 4 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | LF24-MFT | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
304400 | GIB131.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 35 Nm |  | 7 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...25 mm | no |  | GM24A-MP |  |  | for 3-point control, AC only¦ | [10 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304405 | GIB164.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 35 Nm |  | 8 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...25 mm | no |  | GM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304235 | RCM-222 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 10 Nm |  |  |  |  | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | NM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301627 | AM24 RS | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304247 | RCP-219 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301791 | NM230-2 BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301796 | NM230-2-C7 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301470 | DAG1.P1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 3 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | GM24A-TP | P1000A |  |  | GM24A-MP-TP | P1000A |  | for 3-point control, AC only¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301632 | AM24-MFT | [30 empty] | Belimo |  |  | AC/DC 24 V |  | multifunctional | 75 s | 300 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A-MP | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301465 | DAF1.06 | [30 empty] | Joventa |  |  | AC 24 V | 55 dB(A) | Open-close | 10 s | 40 s | 6 Nm |  | 9.8 VA | 1.2 m (halogen-free) | yes |  |  | IP54 | 93° |  |  | 10...16 mm |  |  | NF24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304397 | GEB331.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 15 Nm |  | 3 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | SM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301788 | NM230/300 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301311 | 227-024-05-S1 | [30 empty] | Gruner |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 100 s |  | 5 Nm |  | 4 VA | 1 m (halogen-free) |  | 1 x SPDT |  | IP54 | 95° |  |  | 8...20 mm |  |  | LM24A-S |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Gruner\
304402 | GIB136.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 35 Nm |  | 7 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...25 mm | no |  | GM24A-MP | S2A |  | for 3-point control, AC only¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304407 | GIB331.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 35 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...25 mm | no | [15 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301634 | AM24-MFT2 BL | [30 empty] | Belimo |  |  | AC/DC 24 V |  | multifunctional | 75 s | 300 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A-MP | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304242 | RCP-119 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301629 | AM24/500 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  | 5 m |  |  |  | IP54 | [6 empty] | SM24A | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301462 | DAB1.4C | [30 empty] | Joventa |  |  | AC 24 V | 35 dB(A) | 3-point | 35 s |  | 2 Nm |  | 1.8 W | Terminal |  |  |  | IP42 | 93° |  |  | 8...13 mm | gear disengagement |  | TMC24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304237 | RCM-232 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 15 Nm |  |  |  |  | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | SM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301798 | NM230-2-F1/300 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM230A-F | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301467 | DAF2.06 | [30 empty] | Joventa |  |  | AC 230 V | 55 dB(A) | Open-close | 10 s | 40 s | 6 Nm |  | 11 VA | 1.2 m (halogen-free) | yes |  |  | IP54 | 93° |  |  | 10...16 mm |  |  | NFA |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304244 | RCP-129 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301472 | DAG1.S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 3 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | GM24A-MP-TP | S2A |  | for 3-point control, AC only¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301303 | BT-04P1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | modulating | 30 s |  | 4 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP55 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank |  | LF24-MFT | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301793 | NM230-2 SSB | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301300 | BT-04A2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | Open-close | 30 s |  | 4 Nm |  | 9 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank |  | LF230 | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
304399 | GEB336.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 15 Nm |  | 3 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 6.4...20 mm | gear disengagement |  | SM230A-S |  |  |  | SM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301631 | AM24LON | [30 empty] | Belimo |  |  | AC/DC 24 V |  | LonWorks | 75 s | 300 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24ALON | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304409 | GIB336.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 35 Nm |  | 5 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...25 mm | no | [15 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301308 | BTP-04F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 30 s |  | 4 Nm |  | 9 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301636 | AM24-S | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM24A-S | Z-SMA |  |  | SM24A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301790 | NM230-2 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304404 | GIB163.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 35 Nm |  | 8 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...25 mm | no |  | GM24A-MP | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301626 | AM24 NC | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301464 | DAD1.4C | [30 empty] | Joventa |  |  | AC 24 V | 35 dB(A) | 3-point | 72 s |  | 4 Nm |  | 2.2 W | Terminal |  |  |  | IP42 | 93° |  |  | 8...13 mm | gear disengagement |  | LM24A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301305 | BTP-04A1E | [30 empty] | Elodrive |  |  | AC/DC 24 V | 35 dB(A) | Open-close | 30 s |  | 4 Nm |  | 6 VA | 0.9 m | yes |  |  | IP66 | 95° |  |  | 8...20 mm | hand crank |  | LF24-MFT | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Elodrive\
301474 | DAG2.P1 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 4.5 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | GM230A-TP | P1000A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304406 | GIB166.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 35 Nm |  | 8 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...25 mm | no |  | GM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | GM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304246 | RCP-212 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304239 | RCM-520 | [30 empty] | Newenta |  |  | AC 100...230 V |  | modulating |  |  | 10 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | NM230ASR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301469 | DAG1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 3 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM24A-TP |  |  |  | GM24A-MP-TP |  |  | for 3-point control, AC only¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301787 | NM230 SW | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301628 | AM24 RT | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304241 | RCP-113 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301310 | BTP-04P2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | modulating | 30 s |  | 4 Nm |  | 9.5 VA | 0.9 m | yes |  |  | IP66 | 95° | DC 0(2)...10 V | DC 0(2)...10 V | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301638 | AM24-S H | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  |  |  | 2 x SPDT |  | IP54 | [6 empty] | SM24A-S | Z-SMA |  |  | SM24A | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301795 | NM230-2/300 BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304243 | RCP-123 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
304401 | GIB135.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 35 Nm |  | 7 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  | 1 kΩ | 8...25 mm | no |  | GM24A-MP | P1000A |  | for 3-point control, AC only¦ | GM24A-MP | S2A |  | for 3-point control, AC only¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 20 | EU\Competitors valves retrofit\Air solution\Siemens\
304236 | RCM-230 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 15 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | SM24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301302 | BT-04F2E | [30 empty] | Elodrive |  |  | AC 120...230 V | 35 dB(A) | 3-point | 30 s |  | 4 Nm |  | 9 VA | 0.9 m | yes |  |  | IP55 | 95° |  |  | 8...20 mm | hand crank | [15 empty] | 30 | EU\Competitors valves retrofit\Air solution\Elodrive\
301792 | NM230-2 HG | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301797 | NM230-2-F | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM230A-F | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304248 | RCP-220 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301471 | DAG1.P2 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 3 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | GM24A-TP | P140A |  |  | GM24A-MP-TP | P140A |  | for 3-point control, AC only¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301633 | AM24-MFT2 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | multifunctional | 75 s | 300 s | 18 Nm | [6 empty] | IP54 | [6 empty] | SM24A-MP | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301466 | DAF1.06S | [30 empty] | Joventa |  |  | AC 24 V | 55 dB(A) | Open-close | 10 s | 40 s | 6 Nm |  | 9.8 VA | 1.2 m (halogen-free) | yes | 1 x SPDT |  | IP54 | 93° |  |  | 10...16 mm |  |  | NF24A-S2 |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
301650 | FM220 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 200 s |  | 10 Nm |  | 44 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...16 mm | no |  | NFA | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304413 | GLB161.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 10 Nm |  | 3 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | NM24A-MP |  |  |  | NM24A-SR | [9 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
304258 | RCP-510 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301312 | 227-230-05 | [30 empty] | Gruner |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 150 s |  | 5 Nm |  | 5.5 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | LM230A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Gruner\
301640 | AM24-SR BL | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304418 | GLB332.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 10 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  | 1 kΩ | 8...16 mm | gear disengagement |  | NM230A | P1000A | [12 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301804 | NM24 H | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m |  |  |  | IP42 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301481 | DAL2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM230A-TP |  |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301811 | NM24-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304252 | RCP-232 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301322 | 228C-024-05 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | modulating | 40 s | 75 s | 5 Nm |  |  | 0.9 m | yes |  |  | IP54 | 100° | DC 0(2)...10 V | DC 0(2)...10 V | 8...16 mm | no |  | NF24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
301799 | NM230-C7 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM230A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301483 | DAL2.P2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | GM230A-TP | P140A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301476 | DAG2.S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 4.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM230A-TP | S2A |  | for 3-point control get in touch with your local Belimo support¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304415 | GLB164.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 10 Nm |  | 3 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | NM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301645 | AM24-SR SW | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304420 | GMA121.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 6.4...20 mm | hand crank | piggyback | NF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301478 | DAL1.P1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | GM24A-TP | P1000A |  |  | GM24A-MP-TP | P1000A |  | for 3-point control, AC only¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304260 | RCP-519 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304410 | GLB131.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 10 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301647 | AM24-SR-T | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm |  |  | Terminal |  |  |  | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR-TP | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301317 | 228-024-05-S1 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 40 s | 75 s | 5 Nm |  | 6.5 VA | 0.9 m | yes | 1 x SPDT |  | IP54 | 100° |  |  | 8...16 mm | no |  | NF24A-S2 | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Gruner\
301314 | 227C-024-05 | [30 empty] | Gruner |  |  | AC/DC 24 V | 35 dB(A) | modulating | 100 s |  | 5 Nm |  | 3.5 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0(2)...10 V | 8...20 mm |  |  | LM24A-SR |  |  | Connection: cable 1 m, PVC¦ | LM24A-MP |  |  | Connection: cable 1 m, PVC¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Gruner\
301806 | NM24 SW | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m |  |  |  | IP42 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301642 | AM24-SR H | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301485 | DAN1.SN | [30 empty] | Joventa |  |  | AC/DC 24 V | 40 dB(A) | 2- / 3-point | 35 s |  | 4 Nm |  | 4.1 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° |  |  | 6...16 mm | gear disengagement |  | LMC24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304257 | RCP-429 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304254 | RCP-413 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301801 | NM230-F BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM230A-F | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301324 | 231D2-024-15 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 15 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | [5 empty] | SM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
301319 | 228-230-05 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 40 s | 75 s | 5 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP54 | 100° |  |  | 8...16 mm | no |  | NFA | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Gruner\
304249 | RCP-222 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301803 | NM24 BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m |  |  |  | IP42 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301649 | AM24-T | [30 empty] | Belimo |  |  | AC/DC 24 V |  | 2- / 3-point | 100 s | 150 s | 18 Nm |  |  | Terminal |  |  |  | IP54 | [6 empty] | SM24A-TP | Z-SMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301808 | NM24/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 5 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304422 | GMA131.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | 3-point | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 6.4...20 mm | hand crank | piggyback | NF24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301480 | DAL1.S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | GM24A-MP-TP | S2A |  | for 3-point control, AC only¦ accessory S2A with 2 adjustable switching points¦ | [6 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
304412 | GLB136.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 10 Nm |  | 2 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | NM24A-S |  |  |  | NM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
304417 | GLB331.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 10 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301639 | AM24-SR | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301316 | 228-024-05 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 40 s | 75 s | 5 Nm |  | 6.5 VA | 0.9 m | yes |  |  | IP54 | 100° |  |  | 8...16 mm | no |  | NF24A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Gruner\
301810 | NM24-C1/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301321 | 228-230-05-S2 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 40 s | 75 s | 5 Nm |  | 6.5 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 100° |  |  | 8...16 mm | no |  | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Gruner\
301487 | DAN2.SC | [30 empty] | Joventa |  |  | AC 230 V | 40 dB(A) | Open-close | 35 s |  | 4 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° |  |  | 6...16 mm | gear disengagement |  | LMC230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301644 | AM24-SR RS | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304251 | RCP-230 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 15 Nm | [10 empty] | 6...15 mm |  |  | SM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301482 | DAL2.P1 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | GM230A-TP | P1000A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301475 | DAG2.P2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 140 s |  | 32 Nm |  | 4.5 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | GM230A-TP | P140A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304414 | GLB163.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 10 Nm |  | 3 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | NM24A-MP | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
304259 | RCP-512 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304419 | GLB336.1E | [30 empty] | Siemens |  |  | AC 230 V |  | 3-point | 150 s |  | 10 Nm |  | 2 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | NM230A-S |  |  |  | NM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301805 | NM24 SSB | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m |  |  |  | IP42 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301651 | FM220-S | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 200 s |  | 10 Nm |  | 44 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...16 mm | no |  | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301477 | DAL1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM24A-TP |  |  |  | GM24A-MP-TP |  |  | for 3-point control, AC only¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301646 | AM24-SR-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm |  |  | 1 m (halogen-free) |  |  |  | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301313 | 227-230-05-S1 | [30 empty] | Gruner |  |  | AC 230 V | 35 dB(A) | 2- / 3-point | 150 s |  | 5 Nm |  | 5.5 VA | 1 m (halogen-free) |  | 1 x SPDT |  | IP54 | 95° |  |  | 8...20 mm |  |  | LM230A-S |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Gruner\
304253 | RCP-239 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301323 | 228F-024-05 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | modulating | 150 s |  | 5 Nm |  | 7.5 VA | 0.9 m | yes |  |  | IP54 | 100° | DC 0...10 V adjustable | DC 0(2)...10 V | 8...16 mm | no |  | NF24A-SR |  |  |  | NF24A-SZ | [9 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
301484 | DAL2.S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | GM230A-TP | S2A |  | for 3-point control get in touch with your local Belimo support¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304261 | RCP-520 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301318 | 228-024-05-S2 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 40 s | 75 s | 5 Nm |  | 6.5 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 100° |  |  | 8...16 mm | no |  | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Gruner\
301641 | AM24-SR ERE | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304256 | RCP-423 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301800 | NM230-F | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 75 s | 150 s | 8 Nm |  | 18 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM230A-F | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301479 | DAL1.P2 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 125 s | 160 s | 24 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | GM24A-TP | P140A |  |  | GM24A-MP-TP | P140A |  | for 3-point control, AC only¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
304421 | GMA126.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | Open-close | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 6.4...20 mm | hand crank | piggyback | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
301648 | AM24-S-T | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 100 s | 150 s | 18 Nm |  |  | Terminal |  | 2 x SPDT |  | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-S-TP | Z-SMA |  |  | SM24A-TP | S2A | Z-SMA | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
304416 | GLB166.1E | [30 empty] | Siemens |  |  | AC 24 V |  | modulating | 150 s |  | 10 Nm |  | 3 VA | 0.9 m |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V | DC 0...10 V | 8...16 mm | gear disengagement | selfadaption | NM24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | NM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301315 | 227S-024D-05 | [30 empty] | Gruner |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 20 s | 35 s | 5 Nm |  | 6.5 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | LMC24A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Gruner\
301812 | NM24-C7/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 5 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301643 | AM24-SR NC | [30 empty] | Belimo |  |  | AC/DC 24 V |  | modulating | 150 s |  | 18 Nm | [6 empty] | IP54 |  | DC 2...10 V |  |  |  |  | SM24A-SR | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301486 | DAN1.N | [30 empty] | Joventa |  |  | AC/DC 24 V | 40 dB(A) | 2- / 3-point | 35 s |  | 4 Nm |  | 4.1 VA | Terminal |  |  |  | IP40 | 93° |  |  | 6...16 mm | gear disengagement |  | LMC24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301807 | NM24/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304411 | GLB132.1E | [30 empty] | Siemens |  |  | AC 24 V |  | 3-point | 150 s |  | 10 Nm |  | 2 VA | 0.9 m |  |  |  | IP54 | 95° |  | 1 kΩ | 8...16 mm | gear disengagement |  | NM24A | P1000A | [12 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301809 | NM24/500 SW | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 5 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301802 | NM24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m |  |  |  | IP42 | 95° |  |  | 8...20 mm |  |  | NM24A | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301325 | 231D2-024-15-S1 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 15 Nm |  |  | 0.9 m |  | 1 x SPDT |  | IP54 | 100° | [5 empty] | SM24A-S | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Gruner\
304255 | RCP-419 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304250 | RCP-229 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301320 | 228-230-05-S1 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 40 s | 75 s | 5 Nm |  | 6.5 VA | 0.9 m | yes | 1 x SPDT |  | IP54 | 100° |  |  | 8...16 mm | no |  | NFA-S2 | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Gruner\
304433 | A1H250SS | [30 empty] | Staefa Control System |  |  | AC 24 V |  | Open-close |  |  |  | 250 N |  |  |  | 1 x SPDT |  | IP52 | [6 empty] | SM24A-S |  |  | get in touch with your local Belimo support¦ | [10 empty] | 20 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301496 | DAS2.P1 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement | [15 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304423 | GMA132.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | 3-point | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 90° |  | 1 kΩ | 6.4...20 mm | hand crank | piggyback | NF24A | P1000A-F | [12 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301824 | NM24-SR HC | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304268 | RFM-212 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  |  | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304263 | RCP-529 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301329 | 231D2-230-30 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 150 s |  | 30 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | [5 empty] | GM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
304428 | GMA166.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 6.4...20 mm | hand crank |  | NF24A-SZ-S2 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301498 | DAS2.S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement | [15 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301663 | GM110 | [30 empty] | Belimo |  |  | AC 110 V |  | 2- / 3-point | 80 s |  | 30 Nm | [6 empty] | IP54 | [6 empty] | GM230A | Z-GMA |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301488 | DAN2.SN | [30 empty] | Joventa |  |  | AC 230 V | 40 dB(A) | 3-point | 35 s |  | 4 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° |  |  | 6...16 mm | gear disengagement |  | LMC230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304270 | RFM-222 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 10 Nm |  |  |  |  | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | NM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301658 | FS24-S | [30 empty] | Belimo |  |  | AC 24 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 10 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SF24A-S2 |  |  | Not for fire protection application!¦ | SF24A | S2A-F |  | Not for fire protection application!¦ accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
301814 | NM24-F BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM24A-F | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304265 | RCP-532 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301493 | DAS1.P2 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | NMC24A-MP | P140A | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301336 | 232D2-230-10 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 150 s |  | 10 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | [5 empty] | NM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
304435 | A2H250 | [30 empty] | Staefa Control System |  |  | AC 230 V |  | Open-close |  |  |  | 250 N | [5 empty] | IP52 | [6 empty] | SM230A |  |  | get in touch with your local Belimo support¦ | [10 empty] | 20 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301652 | FM24 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | Open-close | 200 s |  | 10 Nm |  | 10 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...16 mm | no |  | NF24A | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301821 | NM24-SR | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304430 | GMA326.1E | [30 empty] | Siemens |  |  | AC 230 V |  | Open-close | 90 s |  | 7 Nm |  | 7 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 6.4...20 mm | hand crank | piggyback | NFA-S2 |  |  |  | NFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
301331 | 231F-024-30 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | modulating |  |  | 30 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | DC 0(2)...10 V | DC 0(2)...10 V |  |  |  | GM24A-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Gruner\
304425 | GMA161.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 6.4...20 mm | hand crank |  | NF24A-SZ | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Siemens\
301816 | NM24-F/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 5 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM24A-F | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304272 | RFM-232 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 15 Nm |  |  |  |  | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | SM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304262 | RCP-522 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304274 | RFM-520 | [30 empty] | Newenta |  |  | AC 100...230 V |  | modulating |  |  | 10 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | NM230ASR | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301660 | FSL220-S | [30 empty] | Belimo |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 28 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301495 | DAS2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement | [15 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301655 | FS220 | [30 empty] | Belimo |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 28 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SFA |  |  | Not for fire protection application!¦ | [10 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301657 | FS24 | [30 empty] | Belimo |  |  | AC 24 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 10 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SF24A |  |  | Not for fire protection application!¦ | [10 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301490 | DAN2.N | [30 empty] | Joventa |  |  | AC 230 V | 40 dB(A) | 3-point | 35 s |  | 4 Nm |  | 5 VA | Terminal |  |  |  | IP40 | 93° |  |  | 6...16 mm | gear disengagement |  | LMC230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301823 | NM24-SR H | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301326 | 231D2-024-30 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 30 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | [5 empty] | GM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
304432 | A1H250 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | Open-close |  |  |  | 250 N | [5 empty] | IP52 | [6 empty] | SM24A |  |  | get in touch with your local Belimo support¦ | [10 empty] | 20 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301333 | 232-024-10-S1 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 10 Nm |  |  | 0.9 m |  | 1 x SPDT |  | IP54 | 100° | [5 empty] | NM24A-S | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Gruner\
301500 | DBF1.06S | [30 empty] | Joventa |  |  | AC/DC 24 V | 51 dB(A) | 3-point | 60 (90) s |  | 6 Nm |  | 14 VA | 1.2 m (halogen-free) | yes | 1 x SPDT |  | IP54 | 93° |  |  | 10...16 mm |  |  | NF24A-3 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
301818 | NM24-F-C7/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 3 m (halogen-free) |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM24A-F | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304427 | GMA164.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° | DC 0...10 V adjustable | DC 0...10 V | 6.4...20 mm | hand crank |  | NF24A-MP | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | NF24A-SZ | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301328 | 231D2-230-15-S1 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 150 s |  | 15 Nm |  |  | 0.9 m |  | 1 x SPDT |  | IP54 | 100° | [5 empty] | SM230A-S | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Gruner\
301662 | FSL24-S | [30 empty] | Belimo |  |  | AC 24 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 8 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301813 | NM24-F | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM24A-F | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301497 | DAS2.P2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement | [15 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304269 | RFM-220 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 10 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | NM24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301338 | 238-024-15 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 15 Nm |  | 8 VA | 0.9 m | yes |  |  | IP54 | 100° |  |  | 9...20 mm | hand crank |  | SF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
301492 | DAS1.P1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | NMC24A-MP | P1000A | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304267 | RFM-210 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | LM24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
304264 | RCP-530 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 15 Nm | [10 empty] | 6...15 mm |  |  | SM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
304424 | GMA136.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | 3-point | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 6.4...20 mm | hand crank | piggyback | NF24A-3 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [10 empty] | 19 | EU\Competitors valves retrofit\Air solution\Siemens\
301335 | 232D2-024-10-S1 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 10 Nm |  |  | 0.9 m |  | 1 x SPDT |  | IP54 | 100° | [5 empty] | NM24A-S | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Gruner\
301820 | NM24-MFT2 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | multifunctional | 75 s | 300 s | 8 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A-MP | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301825 | NM24-SR KC | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304429 | GMA321.1E | [30 empty] | Siemens |  |  | AC 230 V |  | Open-close | 90 s |  | 7 Nm |  | 7 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 6.4...20 mm | hand crank | piggyback | NFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Siemens\
301330 | 231F-024-15 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | modulating |  |  | 15 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | DC 0(2)...10 V | DC 0(2)...10 V |  |  |  | SM24A-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Gruner\
304273 | RFM-510 | [30 empty] | Newenta |  |  | AC 100...230 V |  | modulating |  |  | 5 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | LM230ASR | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301654 | FM24-SR | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 200 s |  | 10 Nm |  | 15 VA | 1 m | yes |  |  | IP54 | 90° | DC 0...10 V | DC 2...10 V | 10...20 mm | no |  | NF24A-SR | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301489 | DAN2.C | [30 empty] | Joventa |  |  | AC 230 V | 40 dB(A) | Open-close | 35 s |  | 4 Nm |  | 5 VA | Terminal |  |  |  | IP40 | 93° |  |  | 6...16 mm | gear disengagement |  | LMC230A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304271 | RFM-230 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 15 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | SM24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301659 | FSL220 | [30 empty] | Belimo |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 28 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SFA | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301494 | DAS1.S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NMC24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301817 | NM24-F1/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM24A-F | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301664 | GM220 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 180 s |  | 30 Nm |  | 10 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM230A | Z-GMA |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301499 | DBF1.06 | [30 empty] | Joventa |  |  | AC/DC 24 V | 51 dB(A) | 3-point | 60 (90) s |  | 6 Nm |  | 14 VA | 1.2 m (halogen-free) | yes |  |  | IP54 | 93° |  |  | 10...16 mm |  |  | NF24A-3 |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301327 | 231D2-230-15 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 150 s |  | 15 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | [5 empty] | SM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
301815 | NM24-F/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 75 s | 150 s | 8 Nm |  | 3.5 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | NM24A-F | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304431 | A1H20 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | Open-close | 60 s |  |  | 200 N | 6 VA |  |  |  |  | IP52 | [6 empty] | SM24A |  |  | get in touch with your local Belimo support¦ | [10 empty] | 24 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301822 | NM24-SR BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301332 | 232-024-10 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 10 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | [5 empty] | NM24A | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Gruner\
304436 | A2H250SS | [30 empty] | Staefa Control System |  |  | AC 230 V |  | Open-close |  |  |  | 250 N |  |  |  | 1 x SPDT |  | IP52 | [6 empty] | SM230A-S |  |  | get in touch with your local Belimo support¦ | [10 empty] | 19 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
304266 | RCP-539 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301337 | 232D2-230-10-S1 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 150 s |  | 10 Nm |  |  | 0.9 m |  | 1 x SPDT |  | IP54 | 100° | [5 empty] | NM230A-S | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Gruner\
301653 | FM24-S | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | Open-close | 200 s |  | 10 Nm |  | 10 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...16 mm | no |  | NF24A-S2 |  |  |  | NF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301334 | 232D2-024-10 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 10 Nm |  |  | 0.9 m |  |  |  | IP54 | 100° | [5 empty] | NM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
301661 | FSL24 | [30 empty] | Belimo |  |  | AC 24 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 8 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SF24A | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304426 | GMA163.1E | [30 empty] | Siemens |  |  | AC/DC 24 V |  | modulating | 90 s |  | 7 Nm |  | 5 VA | 0.9 m | yes |  |  | IP54 | 90° | DC 0...10 V adjustable | DC 0...10 V | 6.4...20 mm | hand crank |  | NF24A-MP |  |  |  | NF24A-SZ | [9 empty] | 18 | EU\Competitors valves retrofit\Air solution\Siemens\
301819 | NM24-MFT | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | multifunctional | 75 s | 300 s | 8 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NM24A-MP | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301501 | DM1.1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 7.5 VA | Terminal |  |  |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM24A-SR-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301656 | FS220-S | [30 empty] | Belimo |  |  | AC 230 V | 50 dB(A) | Open-close | 90 s |  | 11 Nm |  | 28 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...18 mm | hand crank |  | SFA-S2 |  |  | Not for fire protection application!¦ | SFA | S2A-F |  | Not for fire protection application!¦ accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
301491 | DAS1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 30 s | 45 s | 8 Nm |  | 6.5 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NMC24A-MP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304275 | RFM-530 | [30 empty] | Newenta |  |  | AC 100...230 V |  | modulating |  |  | 15 Nm | [8 empty] | DC 0...10 V |  | 6...15 mm |  |  | SM230ASR | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304448 | AS2D15 | [30 empty] | Staefa Control System |  |  | AC 230 V |  | 3-point |  |  | 15 Nm | [13 empty] | SM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301675 | GM24-MFT2 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | multifunctional | 120 s | 300 s | 30 Nm |  |  | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM24A-MP | Z-GMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301347 | ML6161E2005 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | 3-point | 110 s |  | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° |  |  | 9.5...12.7 mm | no |  | LM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
304280 | RFP-129 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301504 | DM1.1FS | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | modulating | 90 s |  | 16 Nm |  | 12 VA | Terminal | yes | 2 x SPDT |  | IP54 | 93° | DC 0...10 V | DC 0...10 V | 10...20 mm | hand crank |  | SF24A-SZ-S2 |  |  |  | SF24A-SZ | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301503 | DM1.1FK | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | modulating | 90 s |  | 16 Nm |  | 12 VA | 1 m (halogen-free) | yes |  |  | IP54 | 93° | DC 0...10 V | DC 0...10 V | 10...20 mm | hand crank |  | SF24A-SZ |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301339 | 238-024-15-S2 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | Open-close | 150 s |  | 15 Nm |  | 8 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 100° |  |  | 9...20 mm | hand crank |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Gruner\
304287 | RFP-230 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 15 Nm | [10 empty] | 6...15 mm |  |  | SM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
304282 | RFP-212 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301834 | NM24-SR-F HG | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | NM24A-SR-F | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301506 | DM1.3 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 7.5 VA | Terminal |  |  |  | IP54 | 93° | DC 0...20 V Phase-cut / 0...135 Ω | DC 0...10 V | 10...20 mm | gear disengagement |  | SM24A-PC |  |  |  | SM24A-R9 | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301668 | GM24 BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 135 s |  | 30 Nm |  | 6 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM24A | Z-GMA |  |  | GM24A-MP | Z-GMA |  | for 3-point control, AC only¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
304277 | RFP-113 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301826 | NM24-SR SW | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301677 | GM24-SR BL | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  | 7 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301346 | ML6161B2024 | [30 empty] | Honeywell |  |  | AC 24 V |  |  | 90 s | [15 empty] | LM24A-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
304445 | AS1D8 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | 3-point |  |  | 8 Nm |  |  | 1 m | [7 empty] | 8...20 mm |  |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301511 | DM2.5S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 80 s |  | 16 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304440 | AS1D15 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | 3-point |  |  | 15 Nm | [13 empty] | SM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301670 | GM240 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 180 s |  | 30 Nm |  | 10 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM230A | Z-GMA |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301341 | 238C-024-15 | [30 empty] | Gruner |  |  | AC/DC 24 V |  | modulating | 150 s |  | 15 Nm |  | 9 VA | 0.9 m | yes |  |  | IP54 | 100° | DC 0...10 V adjustable | DC 0(2)...10 V | 9...20 mm | hand crank |  | SF24A-SR |  |  |  | SF24A-SZ | [9 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
301665 | GM220 BL | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 80 s |  | 30 Nm |  | 10 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM230A | Z-GMA |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301508 | DM2.2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304284 | RFP-220 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301836 | NM24-SRS | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-MP | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301505 | DM1.1S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 7.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM24A-SR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304442 | AS1D15FS/A | [30 empty] | Staefa Control System |  |  | AC 24 V |  | Open-close |  |  | 15 Nm |  |  | 1 m | yes | 2 x SPDT |  |  | 95° | [5 empty] | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301828 | NM24-SR/300 BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301513 | DMD1.2 | [30 empty] | Joventa |  |  | AC 24 V | 35 dB(A) | modulating | 72 s |  | 4 Nm |  | 2.2 VA | 1.2 m (halogen-free) |  |  |  | IP42 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 8...13 mm | gear disengagement |  | LM24A-SR |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301674 | GM24-MFT | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | multifunctional | 120 s | 300 s | 30 Nm |  |  | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM24A-MP | Z-GMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301672 | GM240/500 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 180 s |  | 30 Nm |  | 10 VA | 5 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM230A | Z-GMA |  | for 3-point control get in touch with your local Belimo support¦ Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301343 | ML4195E1002 | [30 empty] | Honeywell |  |  | AC 230 V | 45 dB(A) | Open-close | 90 s |  | 16 Nm |  | 9 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 8...26 mm | hand crank |  | SFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301831 | NM24-SR-C7 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m (halogen-free) |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | NM24A-SR | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301667 | GM24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 135 s |  | 30 Nm |  | 6 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM24A | Z-GMA |  |  | GM24A-MP | Z-GMA |  | for 3-point control, AC only¦ | [6 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301838 | NMC230-1 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 35 s | 45 s | 4 Nm |  | 11 VA | 1 m |  |  |  | IP42 | 95° |  |  | 8...20 mm |  |  | LMC230A | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301348 | ML6174E2008 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | 3-point | 110 s |  | 8 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° |  |  | 9.5...12.7 mm | no |  | NM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301830 | NM24-SR-1/300 BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301833 | NM24-SR-F BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | NM24A-SR-F | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304286 | RFP-229 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304281 | RFP-210 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301502 | DM1.1F | [30 empty] | Joventa |  |  | AC/DC 24 V | 50 dB(A) | modulating | 90 s |  | 16 Nm |  | 12 VA | Terminal | yes |  |  | IP54 | 93° | DC 0...10 V | DC 0...10 V | 10...20 mm | hand crank |  | SF24A-SZ | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304449 | AS2D15F/A | [30 empty] | Staefa Control System |  |  | AC 230 V |  | Open-close |  |  | 15 Nm |  |  | 1 m | yes |  |  |  | 95° | [5 empty] | SFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301510 | DM2.5 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 80 s |  | 16 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304279 | RFP-123 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
304444 | AS1D30 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | 3-point |  |  | 30 Nm | [13 empty] | GM24A-MP |  |  | for 3-point control, AC only¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301676 | GM24-SR | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  | 7 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301345 | ML6131B2001 | [30 empty] | Honeywell |  |  | AC 24 V |  |  | 15 s |  | 2 Nm | [13 empty] | LMC24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
304278 | RFP-119 | [30 empty] | Newenta |  |  | AC 24 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301340 | 238-230-15 | [30 empty] | Gruner |  |  | AC 230 V |  | Open-close | 150 s |  | 15 Nm |  | 10 VA | 0.9 m | yes |  |  | IP54 | 100° |  |  | 9...20 mm | hand crank |  | SFA | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Gruner\
304288 | RFP-232 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304441 | AS1D15F/A | [30 empty] | Staefa Control System |  |  | AC 24 V |  | Open-close |  |  | 15 Nm |  |  | 1 m | yes |  |  |  | 95° | [5 empty] | SF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301835 | NM24-SR-F/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | NM24A-SR-F | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304283 | RFP-219 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301671 | GM240 BL | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 180 s |  | 30 Nm |  | 10 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM230A | Z-GMA |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301829 | NM24-SR/500 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 5 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301352 | ML6184E1009 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | 3-point | 110 s |  | 17 Nm |  | 5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 10...16 mm | gear disengagement |  | SM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301827 | NM24-SR/300 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 3 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...20 mm |  |  | NM24A-SR | Z-NMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301669 | GM24 H | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 135 s |  | 30 Nm |  | 6 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM24A | Z-GMA |  |  | GM24A-MP | Z-GMA |  | for 3-point control, AC only¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301512 | DMB1.2 | [30 empty] | Joventa |  |  | AC 24 V | 35 dB(A) | modulating | 35 s |  | 2 Nm | [6 empty] | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 8...13 mm | gear disengagement |  | TMC24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301673 | GM24LON | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | LonWorks | 120 s | 300 s | 30 Nm |  |  | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | SM24ALON | Z-GMA | [12 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301507 | DM1.3S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 7.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...20 V Phase-cut / 0...135 Ω | DC 0...10 V | 10...20 mm | gear disengagement |  | SM24A-PC | S2A |  | accessory S2A with 2 adjustable switching points¦ | SM24A-R9 | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301678 | GM24-SR H | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  | 7 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301666 | GM220 H | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 180 s |  | 30 Nm |  | 10 VA | 0.9 m |  |  |  | IP42 | 95° |  |  | 10...20 mm |  |  | GM230A | Z-GMA |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301342 | ML7294E1005 | [30 empty] | Honeywell |  |  | AC/DC 24 V | 45 dB(A) | modulating | 200 s |  | 34 Nm |  | 6 VA | 1 m |  |  |  | IP54 | 95° | DC 0...10 V |  | 10...16 mm | gear disengagement |  | GM24A-SR |  |  |  | GM24A-MP | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301344 | ML4195E1010 | [30 empty] | Honeywell |  |  | AC 230 V | 45 dB(A) | Open-close | 90 s |  | 16 Nm |  | 9 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 8...26 mm | hand crank |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301837 | NMC230 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 35 s | 45 s | 4 Nm |  | 11 VA | 1 m |  |  |  | IP42 | 95° |  |  | 8...20 mm |  |  | LMC230A | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304285 | RFP-222 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301509 | DM2.2S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 80 s | 110 s | 16 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | SM230ASR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301832 | NM24-SR-F | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | modulating | 150 s |  | 8 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8 mm |  |  | NM24A-SR-F | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301690 | KM24-3 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 3-point | 80 s | 110 s | 2.5 Nm |  | 2 VA | Terminal |  |  |  | IP40 | 90° |  |  | 8 mm |  |  | LM24A-F | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304458 | ASXD8 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | modulating |  |  | 8 Nm |  |  | 1 m | [5 empty] | DC 0...10 V |  | 8...20 mm |  |  | NM24A-MP |  |  |  | NM24A-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301357 | ML6661E3010 | [30 empty] | Honeywell |  |  | AC 230 V |  | 3-point | 110 s |  | 4 Nm | [13 empty] | LM230A | [13 empty] | 28 | EU\Competitors valves retrofit\Air solution\Honeywell\
301354 | ML6185E1014 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 120 s |  | 6 Nm |  | 12 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 9.5...12.7 mm | hand crank |  | NF24A-SR-S2 |  |  |  | NF24A-SR | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301685 | KM220 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 15 s | 35 s | 2 Nm |  | 14 VA | Terminal |  |  |  | IP40 | 90° |  |  | 8 mm |  |  | LMC230A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301514 | DMF1.06 | [30 empty] | Joventa |  |  | AC/DC 24 V | 51 dB(A) | modulating | 25 s | 40 s | 6 Nm |  | 12 VA | 1.2 m (halogen-free) | yes |  |  | IP54 | 90° | DC 0(2)...10 V |  | 10...16 mm | no |  | NF24A-SR |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304292 | RFP-419 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304297 | RFP-519 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301519 | DML1.1S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 7.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | GM24A-SR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301524 | DML2.5 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 125 s |  | 24 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301516 | DMG1.1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 200 s |  | 32 Nm |  | 4.5 VA | Terminal |  |  |  | IP40 | 93° | DC 0...10 V | DC 0...10 V | 10...20 mm | gear disengagement |  | GM24A-MP-TP |  |  |  | GM24A-SR-TP | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301839 | NMC24-MF-TP | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | multifunctional |  |  | 10 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NMC24A-MP | Z-NMA | [12 empty] | 31 | EU\Competitors valves retrofit\Air solution\Belimo\
301364 | ML7161A2008 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 90 s |  | 4 Nm |  |  | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 9.5...12.7 mm |  |  | LM24A-SR |  |  |  | LMC24A-SR | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301687 | KM220-S1 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 15 s | 35 s | 2 Nm |  | 15 VA | Terminal |  | 1 x SPDT |  | IP40 | 90° |  |  | 8 mm |  |  | LMC230A-F | S2A | [12 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
301843 | NMQB24-SR | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | modulating | 45 s | 150 s | 8 Nm |  | 12 VA | 1 m |  |  |  | IP42 | 95° | DC 2...10 V | DC 2...10 V | 8...26,7 mm |  |  | NMQ24A-SR | Z-NMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301680 | GM24-SR/300 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  | 7 VA | 3 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301521 | DML1.3S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 7.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...20 V Phase-cut / 0...135 Ω | DC 0...10 V | 10...20 mm | gear disengagement |  | GM24A-SR | S2A | SBG24 | phase-cut control only with SBG24¦ for 0...135 Ω get in touch with your local Belimo support¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
304450 | AS2D15FS/A | [30 empty] | Staefa Control System |  |  | AC 230 V |  | Open-close |  |  | 15 Nm |  |  | 1 m | yes | 2 x SPDT |  |  | 95° | [5 empty] | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301361 | ML6684E1008 | [30 empty] | Honeywell |  |  | AC 230 V | 45 dB(A) | 3-point | 110 s |  | 17 Nm |  | 6 VA | 1 m |  |  |  | IP54 | 95° |  |  | 10...16 mm | gear disengagement |  | SM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301526 | DMN1.2N | [30 empty] | Joventa |  |  | AC/DC 24 V | 40 dB(A) | modulating | 35 s |  | 4 Nm |  | 3.5 VA | Terminal |  |  |  | IP40 | 93° | DC 0...10 V | DC 0...10 V | 6...16 mm | gear disengagement |  | LMC24A-SR |  |  |  | LM24A-SR-TP | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301682 | GM24-SR/500 BL | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  | 7 VA | 5 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304294 | RFP-429 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301841 | NMQ24-MFT | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | multifunctional |  |  | 8 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NMQ24A-MF | Z-NMA | [12 empty] | 31 | EU\Competitors valves retrofit\Air solution\Belimo\
304299 | RFP-522 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301359 | ML6674E3013 | [30 empty] | Honeywell |  |  | AC 230 V |  | 3-point | 110 s |  | 8 Nm | [13 empty] | NM230A | [13 empty] | 28 | EU\Competitors valves retrofit\Air solution\Honeywell\
304289 | RFP-239 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301356 | ML6661E2004 | [30 empty] | Honeywell |  |  | AC 230 V | 45 dB(A) | 3-point | 110 s |  | 4 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° |  |  | 9.5...12.7 mm | no |  | LM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301684 | GM24-SR90/500 BL | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  |  | 5 m |  |  |  | IP54 | 95° | DC 2...10 V / Phase-cut / 0…135 Ω | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA |  | Connection: cable 1 m, PVC¦ | GM24A-SR | SBG24 | Z-GMA | phase-cut control only with SBG24¦ Connection: cable 1 m, PVC¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304452 | AS2D8 | [30 empty] | Staefa Control System |  |  | AC 230 V |  | 3-point |  |  | 8 Nm |  |  | 1 m | [7 empty] | 8...20 mm |  |  | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301689 | KM24+K1 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | Open-close | 15 s | 35 s | 2 Nm |  | 3 VA | Terminal |  |  |  | IP40 | 90° |  |  | 8 mm |  |  | LMC24A | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301523 | DML2.2S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304296 | RFP-512 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 5 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301353 | ML6185E1006 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | Open-close | 120 s |  | 6 Nm |  | 12 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 9.5...12.7 mm | hand crank |  | NF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301518 | DML1.1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 7.5 VA | Terminal |  |  |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | GM24A-SR-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304291 | RFP-413 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301691 | KM24-3+K1 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | 3-point | 80 s | 110 s | 2.5 Nm |  | 2 VA | Terminal |  |  |  | IP40 | 90° |  |  | 8...12 mm |  |  | LM24A | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301679 | GM24-SR SW | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  | 7 VA | 0.9 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304457 | ASUD15F/A | [30 empty] | Staefa Control System |  |  | AC 24 V |  | modulating |  |  | 15 Nm |  |  | 1 m | yes |  |  |  | 95° | DC 2...10 V |  |  |  |  | SF24A-SR | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
304454 | ASU1D15 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | modulating |  |  | 15 Nm |  | 5 VA | [5 empty] | 95° | DC 2...10 V / Phase-cut |  | 10...20 mm |  |  | SM24A-SR |  |  |  | SM24A-PC | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301358 | ML6674E2007 | [30 empty] | Honeywell |  |  | AC 230 V | 45 dB(A) | 3-point | 110 s |  | 8 Nm |  | 4 VA | 1 m |  |  |  | IP54 | 95° |  |  | 9.5...12.7 mm | no |  | NM230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301363 | ML6694E1007 | [30 empty] | Honeywell |  |  | AC 230 V | 45 dB(A) | 3-point | 200 s |  | 34 Nm |  | 6.5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 10...16 mm | gear disengagement | [15 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301355 | ML6194E1008 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | 3-point | 200 s |  | 34 Nm |  | 5 VA | 1 m |  |  |  | IP54 | 95° |  |  | 10...16 mm | gear disengagement |  | GM24A-MP |  |  | for 3-point control, AC only¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
304298 | RFP-520 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
304301 | RFP-530 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 15 Nm | [10 empty] | 6...15 mm |  |  | SM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301515 | DMF1.06S | [30 empty] | Joventa |  |  | AC/DC 24 V | 51 dB(A) | modulating | 25 s | 40 s | 6 Nm |  | 12 VA | 1.2 m (halogen-free) | yes | 1 x SPDT |  | IP54 | 90° | DC 0(2)...10 V |  | 10...16 mm | no |  | NF24A-SR-S2 |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301686 | KM220+K1 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 15 s | 35 s | 2 Nm |  | 14 VA | Terminal |  |  |  | IP40 | 90° |  |  | 8...12 mm |  |  | LMC230A | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304293 | RFP-423 | [30 empty] | Newenta |  |  | AC 230 V |  | 2- / 3-point |  |  | 10 Nm | [10 empty] | 6...15 mm |  |  | NM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301520 | DML1.3 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 7.5 VA | Terminal |  |  |  | IP54 | 93° | DC 0...20 V Phase-cut / 0...135 Ω | DC 0...10 V | 10...20 mm | gear disengagement |  | GM24A-SR | SBG24 |  | phase-cut control only with SBG24¦ for 0...135 Ω get in touch with your local Belimo support¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301681 | GM24-SR/500 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  | 7 VA | 5 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301525 | DML2.5S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 125 s |  | 24 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301362 | ML6684E1016 | [30 empty] | Honeywell |  |  | AC 230 V | 45 dB(A) | 3-point | 110 s |  | 17 Nm |  | 6 VA | 1 m |  | 2 x SPDT |  | IP54 | 95° |  |  | 10...16 mm | gear disengagement |  | SM230A-S |  |  |  | SM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301365 | ML7161A2008+201052B | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 90 s |  | 4 Nm |  |  | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 9.5...12.7 mm |  |  | LM24A-SR | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301683 | GM24-SR90 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 135 s |  | 30 Nm |  |  | 0.9 m |  |  |  | IP54 | 95° | DC 2...10 V / Phase-cut / 0…135 Ω | DC 2...10 V | 10...20 mm |  |  | GM24A-SR | Z-GMA |  |  | GM24A-SR | SBG24 | Z-GMA | phase-cut control only with SBG24¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301840 | NMC24-TP | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close |  |  | 10 Nm |  |  | 1 m |  |  |  | IP54 | 95° |  |  | 8...20 mm |  |  | NMC24A-MP | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304295 | RFP-510 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 5 Nm | [10 empty] | 6...15 mm |  |  | LM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301842 | NMQB24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 52 dB(A) | Open-close | 4 s | 15 s | 8 Nm |  | 20 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8...26,7 mm |  |  | NMQ24A | Z-NMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304461 | EFMA24 | [30 empty] | t.a.c. |  |  | AC 24 V | 45 dB(A) | modulating | 150 s |  | 15 Nm |  | 10 VA | 0.9 m | yes |  |  | IP42 | 95° | DC 2...10 V / Phase-cut | DC 2...10 V | 10…20 mm | hand crank |  | SF24A-SR |  |  |  | SF24A-SR | SBG24 |  | phase-cut control only with SBG24¦ | [6 empty] | 16 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301688 | KM24 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | Open-close | 15 s | 35 s | 2 Nm |  | 3 VA | Terminal |  |  |  | IP40 | 90° |  |  | 8 mm |  |  | LMC24A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301527 | DMN5.2 | [30 empty] | Joventa |  |  | DC 48 V | 40 dB(A) | modulating | 35 s |  | 4 Nm |  | 4.5 VA | Terminal |  |  |  | IP50 | 93° | DC 0...10 V | DC 0...10 V | 6...16 mm | gear disengagement | [15 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301360 | ML6674E3021 | [30 empty] | Honeywell |  |  | AC 230 V |  | 3-point | 110 s |  | 8 Nm | [13 empty] | NM230A | [13 empty] | 28 | EU\Competitors valves retrofit\Air solution\Honeywell\
301844 | NMQB24-SR0 | [30 empty] | Belimo |  |  | AC/DC 24 V | 52 dB(A) | modulating | 2.5 s |  | 4 Nm |  | 23 VA | 1 m |  |  |  | IP54 | 95° | DC 2...10 V | DC 2...10 V | 8...26,7 mm |  |  | LMQ24A-SR | Z-NMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304456 | ASU1D30 | [30 empty] | Staefa Control System |  |  | AC 24 V |  | modulating |  |  | 30 Nm |  | 7 VA | [5 empty] | 95° | DC 2...10 V / Phase-cut |  | 12...20 mm |  |  | GM24A-SR |  |  |  | GM24A-SR | SBG24 |  | phase-cut control only with SBG24¦ | [6 empty] | 16 | EU\Competitors valves retrofit\Air solution\Staefa Control System\
301517 | DMG1.1S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 200 s |  | 32 Nm |  | 4.5 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° | DC 0...10 V | DC 0...10 V | 10...20 mm | gear disengagement |  | GM24A-MP-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | GM24A-SR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304300 | RFP-529 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 10 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | NM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301522 | DML2.2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 125 s | 160 s | 24 Nm |  | 6 VA | Terminal |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement | [15 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304312 | SCP-510-2 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF230 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301695 | LM100 | [30 empty] | Belimo |  |  | AC 110 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 6 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301372 | ML7285E1003 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | Open-close | 120 s |  | 6 Nm |  | 12 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 9.5...12.7 mm | hand crank |  | NF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301377 | ML9184A1000 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 110 s |  | 17 Nm |  | 6 VA | 0.9 m |  |  |  | IP54 | 95° | 0...135 Ω |  | 8...16 mm |  |  | SM24A-R9 | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
304468 | EMS5 | [30 empty] | t.a.c. |  |  | AC 24 V |  | modulating | 150 s |  | 5 Nm |  | 3 VA | 0.9 m |  |  |  | IP50 | 90° | DC 0...10 V |  | 8…16 mm | no |  | LM24A-MP |  |  |  | LM24A-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301700 | LM230 HG | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301367 | ML7174A2001 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 110 s |  | 8 Nm |  |  | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 9.5...12.7 mm | no |  | NM24A-MP | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Honeywell\
304473 | M42/220 V | [30 empty] | t.a.c. |  |  | AC 220 V |  |  | 53 s |  | 2.5 Nm |  | 3.5 VA |  |  |  |  | IP44 | 180° | [5 empty] | LU230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301534 | DMS2.5 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 30 s |  | 8 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301856 | SF230-S | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 110 s |  | 15 Nm |  | 10 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm | no |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304314 | SCP-512-2 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF230-S |  |  |  | LF230 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
301692 | KM24-SL | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 50 s | 180 s | 2 Nm |  | 3 VA | Terminal |  |  |  | IP40 | 45...270° | DC 0...10 V |  | 8 mm |  |  | LU24A-MP | K-LU | ZDB-LU |  | LU24A-MP | K-LU | [8 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
301861 | SM220 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 13 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
304307 | SCM-212-3 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  | yes | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LF24-MFT2 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | LF24-SR | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 20 | EU\Competitors valves retrofit\Air solution\Newenta\
301529 | DMS1.1S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 7.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NMC24A-MP | S2A |  | accessory S2A with 2 adjustable switching points¦ | NM24A-SR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Joventa\
301863 | SM220 H | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 13 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301539 | SA1.10S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 16 s |  | 16 Nm |  | 13 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SMQ24A | S2A |  | for 3-point control get in touch with your local Belimo support¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
304309 | SCP-210-3 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF24 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301369 | ML7174E3013 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 110 s |  | 8 Nm |  |  | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 9.5...12.7 mm |  |  | NM24A-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Honeywell\
301697 | LM230 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301374 | ML7295E1015 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 90 s |  | 16 Nm |  | 10 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 8...26 mm | hand crank |  | SF24A-SZ-S2 |  |  |  | SF24A-SZ | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301702 | LM230/300 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 3 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304475 | MS10-24 | [30 empty] | t.a.c. |  |  | AC 24 V |  | 2- / 3-point |  |  | 10 Nm |  |  | 0.9 m |  |  |  | IP40 | 90° |  |  | 10…16 mm |  |  | NM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301699 | LM230 H | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304302 | RFP-532 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301531 | DMS1.3S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 7.5 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | DC 0...20 V Phase-cut / 0...135 Ω | DC 0...10 V | 10...20 mm | gear disengagement |  | NM24A-SR | S2A | SBG24 | phase-cut control only with SBG24¦ for 0...135 Ω get in touch with your local Belimo support¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Joventa\
301858 | SF24-S | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close | 110 s |  | 15 Nm |  | 7.5 VA | 1 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 10...20 mm | no |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
304304 | SCM-210-2 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  | yes |  |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LF24-MFT2 |  |  |  | LF24-SR | [9 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301376 | ML8195E1011 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | Open-close | 90 s |  | 16 Nm |  | 8 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 8...26 mm | hand crank |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301536 | SA1.10 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 16 s |  | 16 Nm |  | 13 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SMQ24A |  |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301366 | ML7161E2004 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 110 s |  | 4 Nm |  | 7.5 VA | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 9.5...12.7 mm | no |  | LM24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301865 | SM220 RT | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 13 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301538 | SA1.10P2 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 16 s |  | 16 Nm |  | 13 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | SMQ24A | P140A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301371 | ML7284E1006 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 110 s |  | 17 Nm |  | 6 VA | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 10...16 mm | gear disengagement |  | SM24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301694 | KM24-SR+K2 | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 50 s | 180 s | 2 Nm |  | 3 VA | Terminal |  |  |  | IP40 | 45...270° | DC 0...10 V |  | 8...12 mm |  |  | LU24A-MP | K-LU | ZDB-LU |  | LU24A-MP | K-LU | [8 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
304311 | SCP-212-3 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF24-S |  |  |  | LF24 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
301528 | DMS1.1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 7.5 VA | Terminal |  |  |  | IP54 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NMC24A-MP |  |  |  | NM24A-SR-TP | [9 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301860 | SM110 | [30 empty] | Belimo |  |  | AC 110 V | 45 dB(A) | 2- / 3-point | 80 s |  | 15 Nm |  | 5.5 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
304306 | SCM-212-2 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  | yes | 2 x SPDT |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LF24-MFT2 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | LF24-SR | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 21 | EU\Competitors valves retrofit\Air solution\Newenta\
301704 | LM230-F | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM230A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
304313 | SCP-510-3 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF230 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301855 | SF230 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 110 s |  | 15 Nm |  | 10 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm | no |  | SFA | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301533 | DMS2.2S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301373 | ML7295E1007 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 90 s |  | 16 Nm |  | 10 VA | 0.9 m | yes |  |  | IP54 | 90° | DC 0...10 V | DC 0...10 V | 8...26 mm | hand crank |  | SF24A-SZ | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
304472 | M230 | [30 empty] | t.a.c. |  |  | AC 220 V | 45 dB(A) | 2- / 3-point | 80 s |  | 15 Nm |  | 10 VA | 0.9 m |  |  |  |  | 95° | [5 empty] | SM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301378 | N05010 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | modulating | 90/110 s |  | 5 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0(2)...10 V | 8...16 mm | gear disengagement |  | LM24A-SR-TP |  |  |  | LM24A-MP-TP | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301696 | LM100-F | [30 empty] | Belimo |  |  | AC 110 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 6 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM230A-F | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301368 | ML7174E2007 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 110 s |  | 8 Nm |  | 7.5 VA | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 9.5...12.7 mm | no |  | NM24A-SR | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301535 | DMS2.5S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 30 s |  | 8 Nm |  | 6 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° | 0(4)...20 mA | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP | S2A |  | for 0…20 mA use an external 500 Ω resistor¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301693 | KM24-SR | [30 empty] | Belimo |  |  | AC 24 V | 45 dB(A) | modulating | 50 s | 180 s | 2 Nm |  | 3 VA | Terminal |  |  |  | IP40 | 45...270° | DC 0...10 V |  | 8 mm |  |  | LU24A-MP | K-LU | ZDB-LU |  | LU24A-MP | K-LU | [8 empty] | 38 | EU\Competitors valves retrofit\Air solution\Belimo\
304315 | SCP-512-3 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF230-S |  |  |  | LF230 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
301370 | ML7284A1018 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | modulating | 110 s |  | 17 Nm |  |  | 1 m |  |  |  | IP54 | 95° | DC 0...10 V | DC 2...10 V | 9.5...12.7 mm |  |  | SM24A-SR | [13 empty] | 30 | EU\Competitors valves retrofit\Air solution\Honeywell\
301862 | SM220 BL | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 13 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301864 | SM220 HG | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 13 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301530 | DMS1.3 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 7.5 VA | Terminal |  |  |  | IP54 | 93° | DC 0...20 V Phase-cut / 0...135 Ω | DC 0...10 V | 10...20 mm | gear disengagement |  | NM24A-SR | SBG24 |  | phase-cut control only with SBG24¦ for 0...135 Ω get in touch with your local Belimo support¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304308 | SCP-210-2 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF24 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304310 | SCP-212-2 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF24-S |  |  |  | LF24 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
304476 | MS20-24 | [30 empty] | t.a.c. |  |  | AC 24 V |  | 2- / 3-point |  |  | 20 Nm |  |  | 0.9 m |  |  |  | IP54 | 90° |  |  | 8…25 mm |  |  | SM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\t.a.c.\
304303 | RFP-539 | [30 empty] | Newenta |  |  | AC 100...230 V |  | 2- / 3-point |  |  | 15 Nm |  |  |  |  | 2 x SPDT | [5 empty] | 6...15 mm |  |  | SM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301857 | SF24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 45 dB(A) | Open-close | 110 s |  | 15 Nm |  | 7.5 VA | 1 m | yes |  |  | IP54 | 90° |  |  | 10...20 mm | no |  | SF24A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301703 | LM230/300 BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 3 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301701 | LM230 RE | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A | [13 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301698 | LM230 BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301540 | SA1.12 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 8 s |  | 8 Nm |  | 13 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NMQ24A |  |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301532 | DMS2.2 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | modulating | 30 s | 45 s | 8 Nm |  | 6 VA | Terminal |  |  |  | IP40 | 93° | DC 0(2)...10 V | DC 0(2)...10 V | 10...20 mm | gear disengagement |  | NM230ASR-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301375 | ML8195E1003 | [30 empty] | Honeywell |  |  | AC 24 V | 45 dB(A) | Open-close | 90 s |  | 16 Nm |  | 8 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 8...26 mm | hand crank |  | SF24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
304305 | SCM-210-3 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  | yes |  |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LF24-MFT2 |  |  |  | LF24-SR | [9 empty] | 16 | EU\Competitors valves retrofit\Air solution\Newenta\
301859 | SM100 | [30 empty] | Belimo |  |  | AC 110 V | 45 dB(A) | 2- / 3-point | 80 s |  | 15 Nm |  | 5.5 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301537 | SA1.10P1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 16 s |  | 16 Nm |  | 13 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | SMQ24A | P1000A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301866 | SM220 SW | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 13 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301713 | LM24 BL | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 111 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Belimo\
301545 | SA1.23S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 80 s |  | 16 Nm |  | 5.0 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SM24A-S-TP |  |  |  | SM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301382 | N0524-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | 3-point | 110 s |  | 5 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | LM24A-S-TP |  |  |  | LM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301550 | SA2.23 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 80 s |  | 16 Nm |  | 3.6 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SM230A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304483 | MSF16-230-BB | [30 empty] | t.a.c. |  |  | AC 230 V |  | Open-close | 90 s |  | 16 Nm |  | 9 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 8...25 mm | hand crank |  | SFA-S2 |  |  |  | SFA | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301542 | SA1.12P2 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 8 s |  | 8 Nm |  | 13 VA | Terminal |  |  |  | IP54 | 93° |  | 140 Ω | 10...20 mm | gear disengagement |  | NMQ24A | P140A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301379 | N05010-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | modulating | 90/110 s |  | 5 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V adjustable | DC 0(2)...10 V | 8...16 mm | gear disengagement |  | LM24A-SR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | LM24A-MP-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301384 | N10010-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | modulating | 90/110 s |  | 10 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...16 mm | gear disengagement |  | NM24A-SR-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | NM24A-MP-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
304319 | SFP-210-3 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF24 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301873 | SM220-SR/500 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 5 m |  |  |  | IP54 | 95° | DC 1.5...7.5 V |  | 10...20 mm |  |  | SM230ASR | ZR-IF01: Only available at www.djadun.de | Z-SMA | ZR-IF01 Power-/Signal-Converter has to be ordered at www.djadun.de¦ Connection: cable 1 m, PVC¦ | [10 empty] | 42 | EU\Competitors valves retrofit\Air solution\Belimo\
301868 | SM220-SR | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 1.5...7.5 V |  | 10...20 mm |  |  | SM230ASR | ZR-IF01: Only available at www.djadun.de | Z-SMA | ZR-IF01 Power-/Signal-Converter has to be ordered at www.djadun.de¦ | [10 empty] | 44 | EU\Competitors valves retrofit\Air solution\Belimo\
301705 | LM230-F BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM230A-F | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301710 | LM230-S | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A-S | [13 empty] | 36 | EU\Competitors valves retrofit\Air solution\Belimo\
301870 | SM220-SR HG | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 1.5...7.5 V |  | 10...20 mm |  |  | SM230ASR | ZR-IF01: Only available at www.djadun.de | Z-SMA | ZR-IF01 Power-/Signal-Converter has to be ordered at www.djadun.de¦ | [10 empty] | 40 | EU\Competitors valves retrofit\Air solution\Belimo\
304485 | MSF16-24-BB | [30 empty] | t.a.c. |  |  | AC 24 V |  | Open-close | 90 s |  | 16 Nm |  | 8 VA | 0.9 m | yes | 2 x SPDT |  | IP54 | 90° |  |  | 8...25 mm | hand crank |  | SF24A-S2 |  |  |  | SF24A | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\t.a.c.\
304478 | MS5-230 | [30 empty] | t.a.c. |  |  | AC 230 V |  | 2- / 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  |  |  | IP40 | 90° |  |  | 8…16 mm | no |  | LM230A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301547 | SA2.10S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 16 s |  | 16 Nm |  | 13 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° |  |  | 10...20 mm | gear disengagement |  | SMD230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [10 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
304316 | SFM-210-2 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  | yes |  |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LF24-MFT2 |  |  |  | LF24-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304321 | SFP-212-3 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF24-S |  |  |  | LF24 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
304480 | MS5-24 | [30 empty] | t.a.c. |  |  | AC 24 V |  | 2- / 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  |  |  | IP40 | 90° |  |  | 8…16 mm | no |  | LM24A | [13 empty] | 16 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301875 | SM230 H | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 80 s | 150 s | 15 Nm |  | 17 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301381 | N0524 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | 3-point | 110 s |  | 5 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | LM24A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301386 | N1024 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | 3-point | 110 s |  | 10 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | NM24A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Honeywell\
301541 | SA1.12P1 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 8 s |  | 8 Nm |  | 13 VA | Terminal |  |  |  | IP54 | 93° |  | 1 kΩ | 10...20 mm | gear disengagement |  | NMQ24A | P1000A |  | for 3-point control get in touch with your local Belimo support¦ | [10 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301544 | SA1.23 | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 80 s |  | 16 Nm |  | 5.0 VA | Terminal |  |  |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | SM24A-TP | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304482 | MSF16-230 | [30 empty] | t.a.c. |  |  | AC 230 V |  | Open-close | 90 s |  | 16 Nm |  | 9 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 8...25 mm | hand crank |  | SFA | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301549 | SA2.12S | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 8 s |  | 8 Nm |  | 13 VA | Terminal |  | 2 x SPDT |  | IP40 | 93° |  |  | 10...20 mm | gear disengagement | [15 empty] | 32 | EU\Competitors valves retrofit\Air solution\Joventa\
301707 | LM230-F/300 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 3 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM230A-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
301712 | LM24 | [30 empty] | Belimo |  |  | AC/DC 24 V | 35 dB(A) | 2- / 3-point | 80 s | 110 s | 4 Nm |  | 3 VA | 1 m |  |  |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM24A | [13 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301867 | SM220/300 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 90 s | 150 s | 15 Nm |  | 13 VA | 3 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA |  | Connection: cable 1 m, PVC¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301709 | LM230-FS | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 8 mm |  |  | LM230A-F | S1A | [12 empty] | 37 | EU\Competitors valves retrofit\Air solution\Belimo\
301388 | N20010 | [30 empty] | Honeywell |  |  | AC 24 V | 40 dB(A) | modulating | 95 s |  | 20 Nm |  | 6 VA | Terminal |  |  |  | IP54 | 95° | DC 0...10 V / 0...20 mA | DC 0...10 V | 10...27 mm | gear disengagement |  | SM24A-SR-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | SM24A-MP-TP |  |  | for 0…20 mA use an external 500 Ω resistor¦ | [6 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301872 | SM220-SR/300 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 3 m |  |  |  | IP54 | 95° | DC 1.5...7.5 V |  | 10...20 mm |  |  | SM230ASR | ZR-IF01: Only available at www.djadun.de | Z-SMA | ZR-IF01 Power-/Signal-Converter has to be ordered at www.djadun.de¦ Connection: cable 1 m, PVC¦ | [10 empty] | 41 | EU\Competitors valves retrofit\Air solution\Belimo\
304318 | SFP-210-2 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF24 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304323 | SFP-510-3 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF230 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304477 | MS35 | [30 empty] | t.a.c. |  |  | AC 24 V |  | 2- / 3-point | 150 s |  | 35 Nm |  | 10VA | 0.9 m |  |  |  | IP54 | 90° |  |  | 8…25 mm | gear disengagement |  | GM24A |  |  |  | GM24A-MP |  |  | for 3-point control, AC only¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301383 | N10010 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | modulating | 90/110 s |  | 10 Nm |  | 5 VA | Terminal |  |  |  | IP54 | 95° | DC 0...10 V adjustable | DC 0...10 V | 8...16 mm | gear disengagement |  | NM24A-SR-TP |  |  |  | NM24A-MP-TP | [9 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301546 | SA2.10 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 16 s |  | 16 Nm |  | 13 VA | Terminal |  |  |  | IP40 | 93° |  |  | 10...20 mm | gear disengagement |  | SMD230A | [13 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
301869 | SM220-SR BL | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 1.5...7.5 V |  | 10...20 mm |  |  | SM230ASR | ZR-IF01: Only available at www.djadun.de | Z-SMA | ZR-IF01 Power-/Signal-Converter has to be ordered at www.djadun.de¦ | [10 empty] | 40 | EU\Competitors valves retrofit\Air solution\Belimo\
304484 | MSF16-24 | [30 empty] | t.a.c. |  |  | AC 24 V |  | Open-close | 90 s |  | 16 Nm |  | 8 VA | 0.9 m | yes |  |  | IP54 | 90° |  |  | 8...25 mm | hand crank |  | SF24A | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301380 | N05230-2POS | [30 empty] | Honeywell |  |  | AC 230 V | 35 dB(A) | Open-close | 110 s |  | 5 Nm |  | 22 VA | Terminal |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | LM230A-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
304320 | SFP-212-2 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | 2 x SPDT | [5 empty] | 6...15 mm |  |  | LF24-S |  |  |  | LF24 | S2A-F |  | accessory S2A-F with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\Newenta\
301385 | N10230-2POS | [30 empty] | Honeywell |  |  | AC 230 V | 35 dB(A) | Open-close | 140 s |  | 10 Nm |  | 22 VA | Terminal |  |  |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | NM230A-TP | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Honeywell\
301543 | SA1.12S | [30 empty] | Joventa |  |  | AC/DC 24 V | 45 dB(A) | 2- / 3-point | 8 s |  | 8 Nm |  | 13 VA | Terminal |  | 2 x SPDT |  | IP54 | 93° |  |  | 10...20 mm | gear disengagement |  | NMQ24A | S2A |  | for 3-point control get in touch with your local Belimo support¦ accessory S2A with 2 adjustable switching points¦ | [10 empty] | 33 | EU\Competitors valves retrofit\Air solution\Joventa\
301706 | LM230-F FRE | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 1 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM230A-F | [13 empty] | 32 | EU\Competitors valves retrofit\Air solution\Belimo\
301874 | SM230 | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | Open-close | 80 s | 150 s | 15 Nm |  | 17 VA | 0.9 m |  |  |  | IP54 | 95° |  |  | 10...20 mm |  |  | SM230A | Z-SMA | [12 empty] | 34 | EU\Competitors valves retrofit\Air solution\Belimo\
301711 | LM230-S BL | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 111 s | 4 Nm |  | 12 VA | 1 m |  | 1 x SPDT |  | IP54 | 95° |  |  | 6...16 mm |  |  | LM230A-S | [13 empty] | 33 | EU\Competitors valves retrofit\Air solution\Belimo\
301871 | SM220-SR RT | [30 empty] | Belimo |  |  | AC 230 V | 45 dB(A) | modulating | 100 s | 200 s | 15 Nm |  | 5 VA | 0.9 m |  |  |  | IP54 | 95° | DC 1.5...7.5 V |  | 10...20 mm |  |  | SM230ASR | ZR-IF01: Only available at www.djadun.de | Z-SMA | ZR-IF01 Power-/Signal-Converter has to be ordered at www.djadun.de¦ | [10 empty] | 40 | EU\Competitors valves retrofit\Air solution\Belimo\
304317 | SFM-210-3 | [30 empty] | Newenta |  |  | AC/DC 24 V |  | modulating |  |  | 5 Nm |  |  |  | yes |  |  |  |  | DC 0...10 V |  | 6...15 mm |  |  | LF24-MFT2 |  |  |  | LF24-SR | [9 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
301548 | SA2.12 | [30 empty] | Joventa |  |  | AC 230 V | 45 dB(A) | 2- / 3-point | 8 s |  | 8 Nm |  | 13 VA | Terminal |  |  |  | IP40 | 93° |  |  | 10...20 mm | gear disengagement | [15 empty] | 31 | EU\Competitors valves retrofit\Air solution\Joventa\
304479 | MS5-230-BB | [30 empty] | t.a.c. |  |  | AC 230 V |  | 2- / 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  | 2 x SPDT |  | IP40 | 90° |  |  | 8…16 mm | no |  | LM230A-S |  |  |  | LM230A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 17 | EU\Competitors valves retrofit\Air solution\t.a.c.\
304322 | SFP-510-2 | [30 empty] | Newenta |  |  | AC 100...230 V |  | Open-close |  |  | 5 Nm |  |  |  | yes | [6 empty] | 6...15 mm |  |  | LF230 | [13 empty] | 17 | EU\Competitors valves retrofit\Air solution\Newenta\
304481 | MS5-24-BB | [30 empty] | t.a.c. |  |  | AC 24 V |  | 2- / 3-point | 150 s |  | 5 Nm |  | 2 VA | 0.9 m |  | 2 x SPDT |  | IP40 | 90° |  |  | 8…16 mm | no |  | LM24A-S |  |  |  | LM24A | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 18 | EU\Competitors valves retrofit\Air solution\t.a.c.\
301387 | N1024-SW2 | [30 empty] | Honeywell |  |  | AC 24 V | 35 dB(A) | 3-point | 110 s |  | 10 Nm |  | 5 VA | Terminal |  | 2 x SPDT |  | IP54 | 95° |  |  | 8...16 mm | gear disengagement |  | NM24A-S-TP |  |  |  | NM24A-TP | S2A |  | accessory S2A with 2 adjustable switching points¦ | [6 empty] | 33 | EU\Competitors valves retrofit\Air solution\Honeywell\
301708 | LM230-F/500 | [30 empty] | Belimo |  |  | AC 230 V | 35 dB(A) | Open-close | 80 s | 110 s | 4 Nm |  | 12 VA | 5 m |  |  |  | IP54 | 95° |  |  | 8 mm |  |  | LM230A-F |  |  | Connection: cable 1 m, PVC¦ | [10 empty] | 35 | EU\Competitors valves retrofit\Air solution\Belimo\
59438 | P140A | P140A |  |  |  |  | Cable | [15 empty] | IP54 | [5 empty] | PIC_EU_P140A_4C.jpg | P140A | P140A_datasheet_en-gb.pdf | [36 empty] | 296 | EU\Produkte\Zubehör\Elektrisches Zubehör\Rückführpotentiometer\
59441 | P1000A | P1000A |  |  |  |  | Cable | [15 empty] | IP54 | [5 empty] | PIC_EU_P1000A_4C.jpg | P1000A | P1000A_datasheet_en-gb.pdf | [36 empty] | 277 | EU\Produkte\Zubehör\Elektrisches Zubehör\Rückführpotentiometer\
59445 | P10000A | P10000A |  |  |  |  | Cable | [15 empty] | IP54 | [5 empty] | PIC_EU_P10000A_4C.jpg | P10000A | P10000A_datasheet_en-gb.pdf | [36 empty] | 278 | EU\Produkte\Zubehör\Elektrisches Zubehör\Rückführpotentiometer\
59444 | P5000A | P5000A |  |  |  |  | Cable | [15 empty] | IP54 | [5 empty] | PIC_EU_P5000A_4C.jpg | P5000A | P5000A_datasheet_en-gb.pdf | [36 empty] | 281 | EU\Produkte\Zubehör\Elektrisches Zubehör\Rückführpotentiometer\
59451 | S1A | S1A |  |  |  |  | Cable | [15 empty] | IP54 |  | 1 x SPDT |  |  |  | PIC_EU_S1A_4C.jpg | S1A | S1A_datasheet_en-gb.pdf | [36 empty] | 283 | EU\Produkte\Zubehör\Elektrisches Zubehör\Hilfsschalter\
59457 | S2A | S2A |  |  |  |  | Cable | [15 empty] | IP54 |  | 2 x SPDT |  |  |  | PIC_EU_S2A_4C.jpg | S2A | S2A_datasheet_en-gb.pdf | [36 empty] | 275 | EU\Produkte\Zubehör\Elektrisches Zubehör\Hilfsschalter\
5006 | TMC230A-S-F | TMA-190 F01 005 | AC 230 V | 2 W | 0.5 W | 4 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_TMC24A-S-F_4C.jpg | TMC230A-S-F | TMC230A-S-F_datasheet_en-gb.pdf | [36 empty] | 219 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\Open-Close, 3-point\AC 230 V\
4700 | NM24P | NM24P | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 10...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NM24P | NM24P_datasheet_en-gb.pdf | [36 empty] | 399 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
4702 | NM230P-S | NM230P-S | AC 230 V | 2.5 W | 0.6 W | 5.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 10...20 mm | -30°C … 50°C, -40...50°C for actuator with integrated heating |  | PIC_EU_Robustline-Luft-2cable_01_4C.jpg | NM230P-S | NM230P-S_datasheet_en-gb.pdf | [36 empty] | 356 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\Open-Close, 3-point\AC 230 V\
4699 | NMQ24A | NMQ24A | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable | 8 Nm |  |  |  | Max. 95° | 4 s | 90° |  | 56 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 8...26.7 mm | -30°C ... 40°C, Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_NMQ24A_4C.jpg | NMQ24A | NMQ24A_datasheet_en-gb.pdf | [36 empty] | 438 | EU\Products\Air solutions\Very fast runner actuators\NMQ..A (8 Nm)\Open-Close\AC/DC 24 V\
5007 | TMC24A-SR-F | TMA-040 F01 005 | AC/DC 24 V | 1.5 W | 0.4 W | 3 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_TMC24A-SR-F_4C.jpg | TMC24A-SR-F | TMC24A-SR-F_datasheet_en-gb.pdf | [36 empty] | 230 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\modulating\AC/DC 24 V\
4704 | NM24P-SR | NM24P-SR | AC/DC 24 V | 2 W | 0.4 W | 4 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 10...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NM24P-SR | NM24P_datasheet_en-gb.pdf | [36 empty] | 351 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\modulating\AC/DC 24 V\
5004 | TMC230A-F | TMA-070 F01 005 | AC 230 V | 2 W | 0.5 W | 4 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_TMC230A-F_4C.jpg | TMC230A-F | TMC230A-F_datasheet_en-gb.pdf | [36 empty] | 226 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\Open-Close, 3-point\AC 230 V\
4703 | NM230P | NM230P | AC 230 V | 2.5 W | 0.6 W | 5.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 10...20 mm | -30°C … 50°C, -40...50°C for actuator with integrated heating |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NM230P | NM230P_datasheet_en-gb.pdf | [36 empty] | 339 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\Open-Close, 3-point\AC 230 V\
4701 | NM230PSR | NM230PSR | AC 230 V | 3.5 W | 1 W | 6.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 10...20 mm | -30°C … 50°C, -40...50°C for actuator with integrated heating |  | PIC_EU_Robustline-Luft-2cable_01_4C.jpg | NM230PSR | NM230PSR_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\modulating\AC 230 V\
5023 | LMC24A | LMC24A | AC/DC 24 V | 1.5 W | 0.2 W | 2.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A_4C.jpg | LMC24A | LMC24A_datasheet_en-gb.pdf | [36 empty] | 304 | EU\Products\Air solutions\Fast runner actuators\LMC..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
5012 | TMC24A-S | TMC24A-S | AC/DC 24 V | 1.5 W | 0.2 W | 2.5 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_TMC24A-S-neutral_01_4C.jpg | TMC24A-S | TMC24A-S_datasheet_en-gb.pdf | [36 empty] | 325 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
101547 | EF24A-MP | EF24A-MP | AC/DC 24 V | 9.5 W | 4.5 W | 16 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP54 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C ... 50°C |  | PIC_EU_EF24A-MF_4C.jpg | EF24A-MP | EF24A-MP_datasheet_en-gb.pdf | [36 empty] | 362 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\modulating, MP\AC/DC 24 V\
5020 | TF230-S | TF230-S | AC 230 V | 2.5 W | 1.5 W | 5 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <25 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP42 | selectable by mounting L / R | 1 x SPDT | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF-S-neutral_01_4C.jpg | TF230-S | TF230-S_datasheet_en-gb.pdf | [36 empty] | 354 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\Open-Close\AC 230 V\
102117 | LHK24A-SR100 | LHK24A-SR100 | AC/DC 24 V | 7 W | 3 W | 14 VA | Cable |  |  | 150 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C ... 50°C |  | PIC_EU_LHK24A-MF100_4C.jpg | LHK24A-SR100 | SHK24A-SR100_datasheet_en-gb.pdf | [36 empty] | 249 | EU\Products\Air solutions\SuperCap-Linear actuators\LHK..A (150 N)\modulating\AC/DC 24 V\
4708 | NM230A-S | NM230A-S | AC 230 V | 2.5 W | 0.6 W | 5.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM230A-S_4C.jpg | NM230A-S | NM230A-S_datasheet_en-gb.pdf | [36 empty] | 351 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC 230 V\
102364 | SF24A-MOD | SF24A-MOD | AC/DC 24 V | 8.5 W | 3.5 W | 11 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | communicative |  |  |  |  | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C ... 50°C |  | PIC_EU_SF-Connector-neutral_01_4C.jpg | SF24A-MOD | SF24A-MOD_datasheet_en-gb.pdf | [36 empty] | 349 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\modulating, MOD\AC/DC 24 V\
5008 | TMC230A-S | TMC230A-S | AC 230 V | 2 W | 0.5 W | 4 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_TMC230A-S-neutral_01_4C.jpg | TMC230A-S | TMC230A-S_datasheet_en-gb.pdf | [36 empty] | 322 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\Open-Close, 3-point\AC 230 V\
4713 | NM24A | NM24A | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A_4C.jpg | NM24A | NM24A_datasheet_en-gb.pdf | [36 empty] | 555 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
59957 | LF24-SR | LF24-SR | AC/DC 24 V | 2.5 W | 1 W | 5 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 30 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 8...16 mm | -30°C ... 50°C |  | PIC_EU_LF-neutral_01_4C.jpg | LF24-SR | LF24-SR_datasheet_en-gb.pdf | [36 empty] | 365 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\modulating\AC/DC 24 V\
5017 | TF230 | TF230 | AC 230 V | 2.5 W | 1.5 W | 5 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <25 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP42 | selectable by mounting L / R |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF230_4C.jpg | TF230 | TF230_datasheet_en-gb.pdf | [36 empty] | 365 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\Open-Close\AC 230 V\
102114 | LHK24A-1-100 | LHK24A-1-100 | AC/DC 24 V | 7 W | 3 W | 14 VA | Cable |  |  | 150 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C ... 50°C |  | PIC_EU_LHK24A-MF100_4C.jpg | LHK24A-1-100 | SHK24A-1-100_datasheet_en-gb.pdf | [36 empty] | 248 | EU\Products\Air solutions\SuperCap-Linear actuators\LHK..A (150 N)\Open-Close\AC/DC 24 V\
4716 | SM24P-SR | SM24P-SR | AC/DC 24 V | 2 W | 0.4 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | SM24P-SR | SM24P-SR_datasheet_en-gb.pdf | [36 empty] | 367 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\modulating\AC/DC 24 V\
4705 | NM24P-S | NM24P-S | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 10...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-2cable_01_4C.jpg | NM24P-S | NM24P_datasheet_en-gb.pdf | [36 empty] | 357 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
5022 | TF230-SR | TF230-SR | AC 230 V | 2.5 W | 2 W | 5.5 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <25 s / 90° | 50 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP42 | selectable with switch L / R |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF-S-neutral_01_4C.jpg | TF230-SR | TF230-SR_datasheet_en-gb.pdf | [36 empty] | 377 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\modulating\AC 230 V\
59976 | ZDB-LU | ZDB-LU | [26 empty] | PIC_EU_ZDB-LU_Rotation limiter_BW.jpg | ZDB-LU | [37 empty] | 184 | EU\Products\Accessories\Mechanical accessories\Air solutions\Angle of rotation limiter\
59954 | LF24-S | LF24-S | AC/DC 24 V | 5 W | 2.5 W | 7 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 40...75 s | 90° | <20 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 1 x SPDT | Universal spindle clamp 8...16 mm | -30°C ... 50°C |  | PIC_EU_LF24-S_4C.jpg | LF24-S | LF24-S_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\Open-Close\AC/DC 24 V\
4710 | NM24A-SR | NM24A-SR | AC/DC 24 V | 2 W | 0.4 W | 4 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-SR_4C.jpg | NM24A-SR | NM24A-SR_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating\AC/DC 24 V\
61834 | SMD230A | SMD230A | AC 230 V | 4.5 W | 1 W | 8 VA | Cable | 16 Nm |  |  |  | Max. 95° | 20 s | 90° |  | 55 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SMD230A_4C.jpg | SMD230A | SMD230A_datasheet_en-gb.pdf | [36 empty] | 349 | EU\Products\Air solutions\Very fast runner actuators\SMD..A (16 Nm)\Open-Close, 3-point\AC 230 V\
5010 | TMC24A | TMC24A | AC/DC 24 V | 1.5 W | 0.2 W | 2.5 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_TMC24A-neutral_01_4C.jpg | TMC24A | TMC24A_datasheet_en-gb.pdf | [36 empty] | 307 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
102361 | LM24A-MOD | LM24A-MOD | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | communicative |  |  |  |  | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C ... 50°C |  | PIC_EU_LM24A-MOD_4C.jpg | LM24A-MOD | LM24A-MOD_datasheet_en-gb.pdf | [36 empty] | 320 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating, MOD\AC/DC 24 V\
5019 | TF24-S | TF24-S | AC/DC 24 V | 2.5 W | 1.5 W | 5 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <25 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP42 | selectable by mounting L / R | 1 x SPDT | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF24-S_4C.jpg | TF24-S | TF24-S_datasheet_en-gb.pdf | [36 empty] | 372 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\Open-Close\AC/DC 24 V\
102116 | LHK24A-SZ100 | LHKA-6L0 001 AEM | AC/DC 24 V | 7 W | 3 W | 14 VA | Cable |  |  | 150 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | modulating | DC 0...10 V |  | DC 0.5...10 V | DC 0.5...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C ... 50°C |  | PIC_EU_LHK24A-MF100_4C.jpg | LHK24A-SZ100 | SHK24A-SZ100_datasheet_en-gb.pdf | [36 empty] | 241 | EU\Products\Air solutions\SuperCap-Linear actuators\LHK..A (150 N)\modulating\AC/DC 24 V\
4707 | NM230A-F | NM230A-F | AC 230 V | 2.5 W | 0.6 W | 5.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_NM230A-F_4C.jpg | NM230A-F | NM230A-F_datasheet_en-gb.pdf | [36 empty] | 331 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC 230 V\
4715 | SM230ASR | SM230ASR | AC 230 V | 3.5 W | 1 W | 6.5 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C ... 50°C |  | PIC_EU_SM230ASR_4C.jpg | SM230ASR | SM230ASR_datasheet_en-gb.pdf | [36 empty] | 386 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating\AC 230 V\
5021 | TF24-SR | TF24-SR | AC/DC 24 V | 2.5 W | 1 W | 4 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <25 s / 90° | 50 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP42 | selectable with switch L / R |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF24-SR_4C.jpg | TF24-SR | TF24-SR_datasheet_en-gb.pdf | [36 empty] | 338 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\modulating\AC/DC 24 V\
4712 | NM24AP5 | NM24AP5 | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24AP5_4C.jpg | NM24AP5 | NM24AP5_datasheet_en-gb.pdf | [36 empty] | 352 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
59956 | LF230-S | LF230-S | AC 230 V | 5 W | 3 W | 7 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 40...75 s | 90° | <20 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 1 x SPDT | Universal spindle clamp 8...16 mm | -30°C ... 50°C |  | PIC_EU_LF230-S_4C.jpg | LF230-S | LF230-S_datasheet_en-gb.pdf | [36 empty] | 359 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\Open-Close\AC 230 V\
5016 | TF24 | TF24 | AC/DC 24 V | 2.5 W | 1.5 W | 5 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <25 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP42 | selectable by mounting L / R |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF24_4C.jpg | TF24 | TF24_datasheet_en-gb.pdf | [36 empty] | 372 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\Open-Close\AC/DC 24 V\
5024 | LMC24A-F | LMC24A-F | AC/DC 24 V | 1.5 W | 0.2 W | 2.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_LMC24A-F_4C.jpg | LMC24A-F | LMC24A-F_datasheet_en-gb.pdf | [36 empty] | 318 | EU\Products\Air solutions\Fast runner actuators\LMC..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
4714 | NM24A-F | NM24A-F | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_NM24A-F_4C.jpg | NM24A-F | NM24A-F_datasheet_en-gb.pdf | [36 empty] | 323 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
61820 | GK24A-MF | GK24A-MF | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 52 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GK24A-MF_01_4C.jpg | GK24A-MF | GK24A-MF_datasheet_en-gb.pdf | [36 empty] | 391 | EU\Products\Air solutions\SuperCap actuators\GK..A (40 Nm)\modulating, MF\AC/DC 24 V\
4709 | NM230ASR | NM230ASR | AC 230 V | 3.5 W | 1 W | 6.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM230ASR_4C.jpg | NM230ASR | NM230ASR_datasheet_en-gb.pdf | [36 empty] | 384 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating\AC 230 V\
102118 | LHK24A-MP100 | LHK24A-MP100 | AC/DC 24 V | 7 W | 3 W | 14 VA | Cable |  |  | 150 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C ... 50°C |  | PIC_EU_SHK24A-MP100_4C.jpg | LHK24A-MP100 | LHK24A-MP100_datasheet_en-gb.pdf | [36 empty] | 328 | EU\Products\Air solutions\SuperCap-Linear actuators\LHK..A (150 N)\modulating, MP\AC/DC 24 V\
5009 | TMC24A-SR | TMC24A-SR | AC/DC 24 V | 1.5 W | 0.4 W | 3 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_TMC24A-neutral_01_4C.jpg | TMC24A-SR | TMC24A-SR_datasheet_en-gb.pdf | [36 empty] | 313 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\modulating\AC/DC 24 V\
4717 | SM24P-S | SM24P-S | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 14...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | SM24P-S | SM24P-S_datasheet_en-gb.pdf | [36 empty] | 367 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
102115 | LHK24A-MF100 | LHKA-4J0 001 A34 | AC/DC 24 V | 7 W | 3 W | 14 VA | Cable |  |  | 150 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C ... 50°C |  | PIC_EU_LHK24A-MF100_4C.jpg | LHK24A-MF100 | LHK24A-MF100_datasheet_en-gb.pdf | [36 empty] | 285 | EU\Products\Air solutions\SuperCap-Linear actuators\LHK..A (150 N)\modulating, MF\AC/DC 24 V\
4706 | NM230A | NM230A | AC 230 V | 2.5 W | 0.6 W | 5.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM230A_4C.jpg | NM230A | NM230A_datasheet_en-gb.pdf | [36 empty] | 377 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC 230 V\
5018 | TF24-3 | TF24-3 | AC/DC 24 V | 2.5 W | 1 W | 4 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <25 s / 90° | 50 dB(A) | 3-point |  |  |  |  | Cable 1 m, 4 x 0.75 mm² | IP42 | selectable with switch L / R |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF24-3_4C.jpg | TF24-3 | TF24-3_datasheet_en-gb.pdf | [36 empty] | 356 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\Open-Close, 3-point\AC 24 V\
59955 | LF230 | LF230 | AC 230 V | 5 W | 3 W | 7 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 40...75 s | 90° | <20 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 8...16 mm | -30°C ... 50°C |  | PIC_EU_LF230_01_4C.jpg | LF230 | LF230_datasheet_en-gb.pdf | [36 empty] | 360 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\Open-Close\AC 230 V\
4711 | NM24A-S | NM24A-S | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-S_4C.jpg | NM24A-S | NM24A-S_datasheet_en-gb.pdf | [36 empty] | 367 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
127845 | SKM230-T-B12 | SKM230-T-B12 | AC 230 V | 16 W | 1.5 W | 24 VA | Terminals | [9 empty] | Open-close | [5 empty] | IP40 |  |  |  | -30°C ... 50°C |  | SKM230-T-B12-4C.jpg | SKM230-T-B12 | SKM230-T-B12_datasheet_en-gb.pdf | [36 empty] | 169 | EU\Products\Air solutions\SuperCap actuators\SKM.. (Modul for CM..K..)\Open-Close\AC 230 V\
4727 | SM24A | SM24A | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A_4C.jpg | SM24A | SM24A_datasheet_en-gb.pdf | [36 empty] | 407 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
62007 | TMC230A | TMC230A | AC 230 V | 2 W | 0.5 W | 4 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_TMC230A-neutral_01_4C.jpg | TMC230A | TMC230A_datasheet_en-gb.pdf | [36 empty] | 311 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\Open-Close, 3-point\AC 230 V\
5030 | LU24A | LU24A | AC/DC 24 V | 1 W | 0.5 W | 2.5 VA | Cable | 3 Nm |  |  |  | ∞ | 150 s | 360° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 12 mm or 8 mm (with insert) | -30°C … 50°C |  | PIC_EU_LU24A_4C.jpg | LU24A | LU24A_datasheet_en-gb.pdf | [36 empty] | 321 | EU\Products\Air solutions\Full-rotation actuators\LU..A (3 Nm)\Open-Close, 3-point\AC/DC 24 V\
5026 | LMC230A-F | LMC230A-F | AC 230 V | 2 W | 0.5 W | 4 VA | Cable | 5 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_LMC24A-F_4C.jpg | LMC230A-F | LMC230A-F_datasheet_en-gb.pdf | [36 empty] | 308 | EU\Products\Air solutions\Fast runner actuators\LMC..A (5 Nm)\Open-Close, 3-point\AC 230 V\
4724 | SM24A-S | SM24A-S | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-S_4C.jpg | SM24A-S | SM24A-S_datasheet_en-gb.pdf | [36 empty] | 386 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
127358 | NM24P-P5 | NM24P-P5 | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 10...20 mm | -30°C ... 50°C |  | PIC_EU_Robustline-Luft-2cable_01_4C.jpg | NM24P-P5 | NM24P-P5_datasheet_en-gb.pdf | [36 empty] | 202 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
4721 | SM230P | SM230P | AC 230 V | 2.5 W | 0.6 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 14...20 mm | -30°C … 50°C -40...50°C for actuator with integrated heating |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | SM230P | SM230P_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\Open-Close, 3-point\AC 230 V\
140727 | NM24A-MOD | NM24A-MOD | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | communicative |  |  |  |  | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C ... 50°C |  | PIC_EU_NM24A-MOD_4C.jpg | NM24A-MOD | NM24A-MOD_datasheet_en-gb.pdf | [36 empty] | 281 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating, MOD\AC/DC 24 V\
5050 | SM230A-TP | SM230A-TP | AC 230 V | 2.5 W | 0.6 W | 6 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM230A-TP_4C.jpg | SM230A-TP | SM230A-TP_datasheet_en-gb.pdf | [36 empty] | 377 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC 230 V\
4729 | GM24A | GM24A | AC/DC 24 V | 4 W | 2 W | 6 VA | Cable | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A_4C.jpg | GM24A | GM24A_datasheet_en-gb.pdf | [36 empty] | 351 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\Open-Close\AC/DC 24 V\
5032 | LU230A | LU230A | AC 230 V | 2 W | 1 W | 4 VA | Cable | 3 Nm |  |  |  | ∞ | 150 s | 360° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 12 mm or 8 mm (with insert) | -30°C … 50°C |  | PIC_EU_LU230A_4C.jpg | LU230A | LU230A_datasheet_en-gb.pdf | [36 empty] | 313 | EU\Products\Air solutions\Full-rotation actuators\LU..A (3 Nm)\Open-Close, 3-point\AC 230 V\
5025 | LMC230A | LMC230A | AC 230 V | 2 W | 0.5 W | 4 VA | Cable | 5 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LMC230A-neutral_01_4C.jpg | LMC230A | LMC230A_datasheet_en-gb.pdf | [36 empty] | 305 | EU\Products\Air solutions\Fast runner actuators\LMC..A (5 Nm)\Open-Close, 3-point\AC 230 V\
4720 | SM230P-S | SM230P-S | AC 230 V | 2.5 W | 0.6 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 14...20 mm | -30°C … 50°C -40...50°C for actuator with integrated heating |  | PIC_EU_Robustline-Luft-2cable_01_4C.jpg | SM230P-S | SM230P-S_datasheet_en-gb.pdf | [36 empty] | 379 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\Open-Close, 3-point\AC 230 V\
4726 | SM230A-S | SM230A-S | AC 230 V | 2.5 W | 0.6 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM230A-S_4C.jpg | SM230A-S | SM230A-S_datasheet_en-gb.pdf | [36 empty] | 374 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC 230 V\
62006 | SF24A-SZ-S2 | SF24A-SZ-S2 | AC/DC 24 V | 5 W | 3 W | 7 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 0.5...10 V | DC 0.5...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-2Kabel-neutral_01_4C.jpg | SF24A-SZ-S2 | SF24A-SZ-S2_datasheet_en-gb.pdf | [36 empty] | 335 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\modulating\AC/DC 24 V\
140735 | SMD24A | SMD24A | AC/DC 24 V | 4 W | 0.5 W | 6.5 VA | Cable | 16 Nm |  |  |  | Max. 95° | 20 s | 90° |  | 55 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 10...20 mm | -30°C ... 50°C |  | PIC_EU_SMD24A_4C.jpg | SMD24A | SMD24A_datasheet_en-gb.pdf | [36 empty] | 219 | EU\Products\Air solutions\Very fast runner actuators\SMD..A (16 Nm)\Open-Close, 3-point\AC/DC 24 V\
5028 | LMC24A-SR-F | LMC24A-SR-F | AC/DC 24 V | 1.5 W | 0.4 W | 3 VA | Cable | 5 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_LMC24A-SR-F_4C.jpg | LMC24A-SR-F | LMC24A-SR-F_datasheet_en-gb.pdf | [36 empty] | 322 | EU\Products\Air solutions\Fast runner actuators\LMC..A (5 Nm)\modulating\AC/DC 24 V\
4723 | SM24AP5 | SM24AP5 | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-S-neutral_4C.jpg | SM24AP5 | SM24AP5_datasheet_en-gb.pdf | [36 empty] | 377 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
59994 | Z-GMA | Z-GMA | [26 empty] | PIC_EU_Z-GMA_Ground plate_BW.jpg | Z-GMA | [37 empty] | 180 | EU\Products\Accessories\Mechanical accessories\Air solutions\Baseplate extension\
4718 | SM24P-P5 | SM24P-P5 | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 14...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-2cable_01_4C.jpg | SM24P-P5 | SM24P-P5_datasheet_en-gb.pdf | [36 empty] | 361 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
5052 | SM24A-TP | SM24A-TP | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-TP_4C.jpg | SM24A-TP | SM24A-TP_datasheet_en-gb.pdf | [36 empty] | 368 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
5049 | SM24A-SR-TP | SM24A-SR-TP | AC/DC 24 V | 2 W | 0.4 W | 4 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-SR-TP_4C.jpg | SM24A-SR-TP | SM24A-SR-TP_datasheet_en-gb.pdf | [36 empty] | 375 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating\AC/DC 24 V\
5027 | LMC24A-SR | LMC24A-SR | AC/DC 24 V | 1.5 W | 0.4 W | 3 VA | Cable | 5 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-SR_4C.jpg | LMC24A-SR | LMC24A-SR_datasheet_en-gb.pdf | [36 empty] | 313 | EU\Products\Air solutions\Fast runner actuators\LMC..A (5 Nm)\modulating\AC/DC 24 V\
127810 | P1000A-F | P1000A-F |  |  |  |  | Cable | [15 empty] | IP54 | [5 empty] | PIC_EU_P1000A-F_4C.jpg | P1000A-F | P1000A-F_datasheet_en-gb.pdf | [36 empty] | 192 | EU\Products\Accessories\Electrical accessories\Feedback potentiometer\
4728 | SM24A-SR | SM24A-SR | AC/DC 24 V | 2 W | 0.4 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-SR_4C.jpg | SM24A-SR | SM24A-SR_datasheet_en-gb.pdf | [36 empty] | 373 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating\AC/DC 24 V\
5031 | LU24A-SR | LU24A-SR | AC/DC 24 V | 1.5 W | 0.5 W | 3 VA | Cable | 3 Nm |  |  |  | 0...330° | 150 s | 360° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Form fit 12 mm or 8 mm (with insert) | -30°C … 50°C |  | PIC_EU_LU24A-SR_4C.jpg | LU24A-SR | LU24A-SR_datasheet_en-gb.pdf | [36 empty] | 325 | EU\Products\Air solutions\Full-rotation actuators\LU..A (3 Nm)\modulating\AC/DC 24 V\
4725 | SM230A | SM230A | AC 230 V | 2.5 W | 0.6 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM230A_4C.jpg | SM230A | SM230A_datasheet_en-gb.pdf | [36 empty] | 374 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC 230 V\
4722 | SM230PSR | SM230PSR | AC 230 V | 3.5 W | 1 W | 6.5 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...20 mm | -30°C … 50°C -40...50°C for actuator with integrated heating |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | SM230PSR | SM230PSR_datasheet_en-gb.pdf | [36 empty] | 385 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\modulating\AC 230 V\
4719 | SM24P | SM24P | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 14...20 mm |  |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | SM24P | SM24P_datasheet_en-gb.pdf | [36 empty] | 365 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
5051 | SM230A-S-TP | SM230A-S-TP | AC 230 V | 2.5 W | 0.6 W | 6 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM230A-S-TP_4C.jpg | SM230A-S-TP | SM230A-S-TP_datasheet_en-gb.pdf | [36 empty] | 375 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC 230 V\
140730 | SM24A-MOD | SM24A-MOD | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | communicative |  |  |  |  | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C ... 50°C |  | PIC_EU_SM24A-MOD_4C.jpg | SM24A-MOD | SM24A-MOD_datasheet_en-gb.pdf | [36 empty] | 288 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating, MOD\AC/DC 24 V\
4730 | GM24A-SR | GM24A-SR | AC/DC 24 V | 4.5 W | 2 W | 6.5 VA | Cable | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-SR_4C.jpg | GM24A-SR | GM24A-SR_datasheet_en-gb.pdf | [36 empty] | 343 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\modulating\AC/DC 24 V\
5033 | LU230ASR | LU230ASR | AC 230 V | 2 W | 1 W | 4 VA | Cable | 3 Nm |  |  |  | 0...330° | 150 s | 360° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Form fit 12 mm or 8 mm (with insert) | -30°C … 50°C |  | PIC_EU_LU230ASR_4C.jpg | LU230ASR | LU230ASR_datasheet_en-gb.pdf | [36 empty] | 348 | EU\Products\Air solutions\Full-rotation actuators\LU..A (3 Nm)\modulating\AC 230 V\
4735 | SMQ24A | SMQ24A | AC/DC 24 V | 15 W | 2 W | 26 VA | Cable | 16 Nm |  |  |  | Max. 95° | 7 s | 90° |  | 63 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_SMQ24A_4C.jpg | SMQ24A | SMQ24A_datasheet_en-gb.pdf | [36 empty] | 316 | EU\Products\Air solutions\Very fast runner actuators\SMQ..A (16 Nm)\Open-Close\AC/DC 24 V\
4750 | SF24A-SR-S2 | SF24A-SR-S2 | AC/DC 24 V | 5 W | 3 W | 7 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-2Kabel-neutral_01_4C.jpg | SF24A-SR-S2 | SF24A-SR-S2_datasheet_en-gb.pdf | [36 empty] | 355 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\modulating\AC/DC 24 V\
5053 | SM24A-S-TP | SM24A-S-TP | AC/DC 24 V | 2 W | 0.2 W | 4 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-S-TP_4C.jpg | SM24A-S-TP | SM24A-S-TP_datasheet_en-gb.pdf | [36 empty] | 382 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
5058 | NM24A-S-TP | NM24A-S-TP | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-S-TP_4C.jpg | NM24A-S-TP | NM24A-S-TP_datasheet_en-gb.pdf | [36 empty] | 334 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
4732 | GM24A-TP | GM24A-TP | AC/DC 24 V | 4 W | 2 W | 6 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-TP_4C.jpg | GM24A-TP | GM24A-TP_datasheet_en-gb.pdf | [36 empty] | 336 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\Open-Close\AC/DC 24 V\
5067 | GK24A-1 | GK24A-1 | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 53 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GK24A-MF_01_4C.jpg | GK24A-1 | GK24A-1_datasheet_en-gb.pdf | [36 empty] | 352 | EU\Products\Air solutions\SuperCap actuators\GK..A (40 Nm)\Open-Close\AC/DC 24 V\
4746 | SF230A-S2 | SF230A-S2 | AC 230 V | 6.5 W | 3.5 W | 18 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-2Kabel-neutral_01_4C.jpg | SF230A-S2 | SF230A-S2_datasheet_en-gb.pdf | [36 empty] | 364 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\Open-Close, 3-point\AC 230 V\
5055 | NM230A-S-TP | NM230A-S-TP | AC 230 V | 2.5 W | 0.6 W | 5.5 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM230A-S-TP_4C.jpg | NM230A-S-TP | NM230A-S-TP_datasheet_en-gb.pdf | [36 empty] | 331 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC 230 V\
4734 | GM230A-TP | GM230A-TP | AC 230 V | 5 W | 2.5 W | 9 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-TP_4C.jpg | GM230A-TP | GM230A-TP_datasheet_en-gb.pdf | [36 empty] | 331 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\Open-Close\AC 230 V\
4736 | LMQ24A | LMQ24A | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable | 4 Nm |  |  |  | Max. 95° | 2.5 s | 90° |  | 54 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...26.7 mm | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_LMQ24A_4C.jpg | LMQ24A | LMQ24A_datasheet_en-gb.pdf | [36 empty] | 332 | EU\Products\Air solutions\Very fast runner actuators\LMQ..A (4 Nm)\Open-Close\AC/DC 24 V\
4731 | GM24A-SR-TP | GM24A-SR-TP | AC/DC 24 V | 4.5 W | 2 W | 6.5 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-SR-TP_4C.jpg | GM24A-SR-TP | GM24A-SR-TP_datasheet_en-gb.pdf | [36 empty] | 337 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\modulating\AC/DC 24 V\
5057 | NM24A-TP | NM24A-TP | AC/DC 24 V | 1.5 W | 0.2 W | 3.5 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-TP_4C.jpg | NM24A-TP | NM24A-TP_datasheet_en-gb.pdf | [36 empty] | 330 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC/DC 24 V\
4749 | SF24A-SZ | SF24A-SZ | AC/DC 24 V | 5 W | 3 W | 7 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 0.5...10 V | DC 0.5...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-1Kabel-neutral_01_4C.jpg | SF24A-SZ | SF24A-SZ_datasheet_en-gb.pdf | [36 empty] | 337 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\modulating\AC/DC 24 V\
5054 | NM230A-TP | NM230A-TP | AC 230 V | 2.5 W | 0.6 W | 5.5 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM230A-TP_4C.jpg | NM230A-TP | NM230A-TP_datasheet_en-gb.pdf | [36 empty] | 334 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\Open-Close, 3-point\AC 230 V\
5060 | SM230ASR-TP | SM230ASR-TP | AC 230 V | 3.5 W | 1 W | 6.5 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM230ASR-TP_4C.jpg | SM230ASR-TP | SM230ASR-TP_datasheet_en-gb.pdf | [36 empty] | 393 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating\AC 230 V\
4751 | SF24A-SR | SF24A-SR | AC/DC 24 V | 5 W | 3 W | 7 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF24A-SR_4C.jpg | SF24A-SR | SF24A-SR_datasheet_en-gb.pdf | [36 empty] | 357 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\modulating\AC/DC 24 V\
5059 | NM24A-SR-TP | NM24A-SR-TP | AC/DC 24 V | 2 W | 0.4 W | 4 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-SR-TP_4C.jpg | NM24A-SR-TP | NM24A-SR-TP_datasheet_en-gb.pdf | [36 empty] | 333 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating\AC/DC 24 V\
4733 | GM230A | GM230A | AC 230 V | 5 W | 2.5 W | 9 VA | Cable | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM230A_4C.jpg | GM230A | GM230A_datasheet_en-gb.pdf | [36 empty] | 333 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\Open-Close\AC 230 V\
4752 | SF24A-S2 | SF24A-S2 | AC/DC 24 V | 5 W | 2.5 W | 7.5 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF24A-S2_4C.jpg | SF24A-S2 | SF24A-S2_datasheet_en-gb.pdf | [36 empty] | 373 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
5068 | GK24A-SR | GK24A-SR | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 53 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GK24A-MF_01_4C.jpg | GK24A-SR | GK24A-SR_datasheet_en-gb.pdf | [36 empty] | 356 | EU\Products\Air solutions\SuperCap actuators\GK..A (40 Nm)\modulating\AC/DC 24 V\
60039 | Z-NMA | Z-NMA | [26 empty] | PIC_EU_Z-NMA_Extension_BW.jpg | Z-NMA | [37 empty] | 187 | EU\Products\Accessories\Mechanical accessories\Air solutions\Baseplate extension\
5056 | NM230ASR-TP | NM230ASR-TP | AC 230 V | 3.5 W | 1 W | 6.5 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM230ASR-TP_4C.jpg | NM230ASR-TP | NM230ASR-TP_datasheet_en-gb.pdf | [36 empty] | 365 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating\AC 230 V\
253690 | CM24-SX-L | CMA-1W0 101 008 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SX-L_4C.jpg | CM24-SX-L | CM24-SX-L_datasheet_en-gb.pdf | [36 empty] | 237 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
4747 | SF230A | SF230A | AC 230 V | 6.5 W | 3.5 W | 18 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF230A_4C.jpg | SF230A | SF230A_datasheet_en-gb.pdf | [36 empty] | 360 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\Open-Close, 3-point\AC 230 V\
60066 | Z-SF | Z-SF | [26 empty] | PIC_EU_Z-SF_BW.jpg | Z-SF | [37 empty] | 165 | EU\Products\Accessories\Mechanical accessories\Air solutions\Baseplate extension\
5504 | NMQ24A-SR | NMQ24A-SR | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable | 8 Nm |  |  |  | Max. 95° | 4 s | 90° |  | 56 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 8...26.7 mm | -30°C … 40°C, Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_NMQ24A-SR_4C.jpg | NMQ24A-SR | NMQ24A-SR_datasheet_en-gb.pdf | [36 empty] | 349 | EU\Products\Air solutions\Very fast runner actuators\NMQ..A (8 Nm)\modulating\AC/DC 24 V\
4759 | NF24A-S2 | NF24A-S2 | AC/DC 24 V | 6 W | 2.5 W | 8.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF24A-S2_4C.jpg | NF24A-S2 | NF24A-S2_datasheet_en-gb.pdf | [36 empty] | 414 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\Open-Close\AC/DC 24 V\
4764 | NF24A | NF24A | AC/DC 24 V | 6 W | 2.5 W | 8.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF24A_4C.jpg | NF24A | NF24A_datasheet_en-gb.pdf | [36 empty] | 378 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\Open-Close\AC/DC 24 V\
255151 | CH24-SX-R100 | CHA-LD0 001 012 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | cw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-SX-R100_4C.jpg | CH24-SX-R100 | CH24-SX-R100_datasheet_en-gb.pdf | [36 empty] | 153 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
4756 | NF230A | NF230A | AC 230 V | 6 W | 2.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF230A_4C.jpg | NF230A | NF230A_datasheet_en-gb.pdf | [36 empty] | 367 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\Open-Close\AC 230 V\
5523 | SHQ24A-SR100 | SHQ24A-SR100 | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable |  |  | 200 N |  |  | 7 s | 100 mm |  | 56 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_SHQ24A-SR100_4C.jpg | SHQ24A-SR100 | SHQ24A-SR100_datasheet_en-gb.pdf | [36 empty] | 330 | EU\Products\Air solutions\(Very)fast running linear actuators\SHQ..A (200 N)\modulating\AC/DC 24 V\
4761 | NF24A-SR-S2 | NF24A-SR-S2 | AC/DC 24 V | 3.5 W | 2.5 W | 5.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF-2Kabel-neutral_01_4C.jpg | NF24A-SR-S2 | NF24A-SR-S2_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\modulating\AC/DC 24 V\
255082 | CH24-SX-L100 | CHA-LD0 001 016 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | ccw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-SX-L100_4C.jpg | CH24-SX-L100 | CH24-SX-L100_datasheet_en-gb.pdf | [36 empty] | 162 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
5506 | SMQ24A-SR | SMQ24A-SR | AC/DC 24 V | 15 W | 2 W | 26 VA | Cable | 16 Nm |  |  |  | Max. 95° | 7 s | 90° |  | 63 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_SMQ24A-SR_4C.jpg | SMQ24A-SR | SMQ24A-SR_datasheet_en-gb.pdf | [36 empty] | 319 | EU\Products\Air solutions\Very fast runner actuators\SMQ..A (16 Nm)\modulating\AC/DC 24 V\
4753 | SF24A-MF | SF24A-MF | AC/DC 24 V | 8.5 W | 3.5 W | 11 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-Connector-neutral_01_4C.jpg | SF24A-MF | SF24A-MF_datasheet_en-gb.pdf | [36 empty] | 423 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\modulating, MF\AC/DC 24 V\
255274 | CH24-SX-R40 | CHA-LK0 001 012 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | cw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-SX-R40_4C.jpg | CH24-SX-R40 | CH24-SX-R40_datasheet_en-gb.pdf | [36 empty] | 147 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
5509 | LMQ24A-MF | LMQ24A-MF | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable | 4 Nm |  |  |  | Max. 95° | 2.5 s | 90° |  | 54 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 40°C |  | PIC_EU_LMQ24A-MF_4C.jpg | LMQ24A-MF | LMQ24A-MF_datasheet_en-gb.pdf | [36 empty] | 359 | EU\Products\Air solutions\Very fast runner actuators\LMQ..A (4 Nm)\modulating, MF\AC/DC 24 V\
255109 | CM24-SX-T-R | CMA-1W0 100 007 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Terminals | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (4-wire) | IP20 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SX-T-R_4C.jpg | CM24-SX-T-R | CM24-SX-T-R_datasheet_en-gb.pdf | [36 empty] | 224 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
4758 | NF24A-SZ-S2 | NF24A-SZ-S2 | AC/DC 24 V | 3.5 W | 2.5 W | 5.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 0.5...10 V | DC 0.5...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF-2Kabel-neutral_01_4C.jpg | NF24A-SZ-S2 | NF24A-SZ-S2_datasheet_en-gb.pdf | [36 empty] | 355 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\modulating\AC/DC 24 V\
4755 | SF24A | SF24A | AC/DC 24 V | 5 W | 2.5 W | 7.5 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF24A_4C.jpg | SF24A | SF24A_datasheet_en-gb.pdf | [36 empty] | 373 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
255081 | CM24-SX-R | CMA-1W0 101 007 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SX-R_4C.jpg | CM24-SX-R | CM24-SX-R_datasheet_en-gb.pdf | [36 empty] | 204 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
5505 | NMQ24A-MF | NMQ24A-MF | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable | 8 Nm |  |  |  | Max. 95° | 4 s | 90° |  | 56 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 8...26.7 mm | -30°C … 40°C |  | PIC_EU_NMQ24A-MF_4C.jpg | NMQ24A-MF | NMQ24A-MF_datasheet_en-gb.pdf | [36 empty] | 348 | EU\Products\Air solutions\Very fast runner actuators\NMQ..A (8 Nm)\modulating, MF\AC/DC 24 V\
4757 | NF230A-S2 | NF230A-S2 | AC 230 V | 6 W | 2.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF230A-S2_4C.jpg | NF230A-S2 | NF230A-S2_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\Open-Close\AC 230 V\
4763 | NF24A-SR | NF24A-SR | AC/DC 24 V | 3.5 W | 2.5 W | 5.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF24A-SR_4C.jpg | NF24A-SR | NF24A-SR_datasheet_en-gb.pdf | [36 empty] | 359 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\modulating\AC/DC 24 V\
5508 | LMQ24A-SR | LMQ24A-SR | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable | 4 Nm |  |  |  | Max. 95° | 2.5 s | 90° |  | 54 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_LMQ24A-SR_4C.jpg | LMQ24A-SR | LMQ24A-SR_datasheet_en-gb.pdf | [36 empty] | 334 | EU\Products\Air solutions\Very fast runner actuators\LMQ..A (4 Nm)\modulating\AC/DC 24 V\
4760 | NF24A-SZ | NF24A-SZ | AC/DC 24 V | 3.5 W | 2.5 W | 5.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 0.5...10 V | DC 0.5...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF_1Kabel-neutral_01_4C.jpg | NF24A-SZ | NF24A-SZ_datasheet_en-gb.pdf | [36 empty] | 343 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\modulating\AC/DC 24 V\
255108 | CM24-SX-T-L | CMA-1W0 100 008 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Terminals | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (4-wire) | IP20 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SX-T-L_4C.jpg | CM24-SX-T-L | CM24-SX-T-L_datasheet_en-gb.pdf | [36 empty] | 212 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
5510 | SF24A-MP | SF24A-MP | AC/DC 24 V | 8.5 W | 3.5 W | 11 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-Connector-neutral_01_4C.jpg | SF24A-MP | SF24A-MP_datasheet_en-gb.pdf | [36 empty] | 459 | EU\Produkte\Lüftungsanwendungen\Federrücklaufantriebe\SF..A (20 Nm)\stetig, MP\AC/DC 24 V\
4762 | NF24A-MF | NF24A-MF | AC/DC 24 V | 7 W | 3.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF-Connector-neutral_01_4C.jpg | NF24A-MF | NF24A-MF_datasheet_en-gb.pdf | [36 empty] | 417 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\modulating, MF\AC/DC 24 V\
255272 | CH24-SX-L40 | CHA-LK0 001 016 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | ccw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-SX-L40_4C.jpg | CH24-SX-L40 | CH24-SX-L40_datasheet_en-gb.pdf | [36 empty] | 144 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
4754 | SF24ALON | SF24ALON | AC/DC 24 V | 8.5 W | 3.5 W | 11 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | communicative |  |  |  |  | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-Connector-neutral_01_4C.jpg | SF24ALON | SF24ALON_datasheet_en-gb.pdf | [36 empty] | 438 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\modulating, LON\AC/DC 24 V\
5507 | SMQ24A-MF | SMQ24A-MF | AC/DC 24 V | 15 W | 2 W | 26 VA | Cable | 16 Nm |  |  |  | Max. 95° | 7 s | 90° |  | 63 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 40°C |  | PIC_EU_SMQ24A_4C.jpg | SMQ24A-MF | SMQ24A-MF_datasheet_en-gb.pdf | [36 empty] | 346 | EU\Products\Air solutions\Very fast runner actuators\SMQ..A (16 Nm)\modulating, MF\AC/DC 24 V\
5554 | SH24A-MF300 | SH24A-MF300 | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-MF-200_4C.jpg | SH24A-MF300 | SH24A-MF300_datasheet_en-gb.pdf | [36 empty] | 366 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating, MF\AC/DC 24 V\
272593 | CH230-L40 | CHA-LJ0 001 008 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable through contact assignment |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH230-L40 | CH230-L40_datasheet_en-gb.pdf | [36 empty] | 129 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\Open-Close, 3-point\AC 230 V\
5558 | LH24A-MF60 | LH24A-MF60 | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF_4C.jpg | LH24A-MF60 | LH24A-MF60_datasheet_en-gb.pdf | [36 empty] | 377 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
5551 | TF24-MFT | TF24-MFT | AC/DC 24 V | 2.5 W | 1 W | 4 VA | Cable | 2.5 Nm | 2.5 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <25 s / 90° | 50 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP42 | selectable with switch L / R |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_TF24-MFT_4C.jpg | TF24-MFT | TF24-MFT_datasheet_en-gb.pdf | [36 empty] | 444 | EU\Products\Air solutions\Spring return actuators\TF.. (2.5 Nm)\modulating, MF\AC/DC 24 V\
4827 | LM24A-SR-TP | LM24A-SR-TP | AC/DC 24 V | 1 W | 0.4 W | 2 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-SR-TP_4C.jpg | LM24A-SR-TP | LM24A-SR-TP_datasheet_en-gb.pdf | [36 empty] | 355 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating\AC/DC 24 V\
5556 | SH24A-MP200 | SH24A-MP200 | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-MP-200_4C.jpg | SH24A-MP200 | SH24A-MP200_datasheet_en-gb.pdf | [36 empty] | 404 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating, MP\AC/DC 24 V\
5553 | SH24A-MF200 | SH24A-MF200 | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-MF-200_4C.jpg | SH24A-MF200 | SH24A-MF200_datasheet_en-gb.pdf | [36 empty] | 366 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating, MF\AC/DC 24 V\
272071 | CH24-L40 | CHA-LG0 001 008 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable through contact assignment |  |  | -30°C … 50°C |  | PIC_EU_CH24-SX-L40_4C.jpg | CH24-L40 | CH24-L40_datasheet_en-gb.pdf | [36 empty] | 131 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\Open-Close, 3-point\AC/DC 24 V\
5539 | LHQ24A-SR100 | LHQ24A-SR100 | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable |  |  | 100 N |  |  | 3.5 s | 100 mm |  | 56 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_LHQ24A-SR100_4C.jpg | LHQ24A-SR100 | [37 empty] | 324 | EU\Products\Air solutions\(Very)fast running linear actuators\LHQ..A (100 N)\modulating\AC/DC 24 V\
5555 | SH24A-MP100 | SH24A-MP100 | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-MP-200_4C.jpg | SH24A-MP100 | SH24A-MP100_datasheet_en-gb.pdf | [36 empty] | 417 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating, MP\AC/DC 24 V\
5552 | SH24A-MF100 | SH24A-MF100 | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-MF100_4C.jpg | SH24A-MF100 | SH24A-MF100_datasheet_en-gb.pdf | [36 empty] | 381 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating, MF\AC/DC 24 V\
5557 | SH24A-MP300 | SH24A-MP300 | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-MP-200_4C.jpg | SH24A-MP300 | SH24A-MP300_datasheet_en-gb.pdf | [36 empty] | 402 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating, MP\AC/DC 24 V\
4826 | LM24A-S-TP | LM24A-S-TP | AC/DC 24 V | 1 W | 0.2 W | 1.5 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-S-TP_4C.jpg | LM24A-S-TP | [37 empty] | 382 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
5559 | LH24A-MF100 | LH24A-MF100 | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF_4C.jpg | LH24A-MF100 | LH24A-MF100_datasheet_en-gb.pdf | [36 empty] | 357 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
69780 | GM24G-MP-T | GM24G-MP-T | AC/DC 24 V | 4 W | 1.6 W | 7 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_GM..G-T-neutral_01_4C.jpg | GM24G-MP-T | GM24G-MP-T_datasheet_en-gb.pdf | [36 empty] | 404 | EU\Products\Air solutions\IP66/NEMA4 actuator\GM..G-T (40 Nm)\modulating, MP\AC/DC 24 V\
5572 | SM24P-MF | SM24P-MF | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | SM24P-MF | SM24P-MF_datasheet_en-gb.pdf | [36 empty] | 397 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\modulating, MF\AC/DC 24 V\
4828 | LM24A-SR-F | LM24A-SR-F | AC/DC 24 V | 1 W | 0.4 W | 2 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_LM24A-SR-F_4C.jpg | LM24A-SR-F | LM24A-SR-F_datasheet_en-gb.pdf | [36 empty] | 308 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating\AC/DC 24 V\
5564 | LH24A-MF100-TP | LH24A-MF100-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF100-TP_4C.jpg | LH24A-MF100-TP | LH24A-MF100-TP_datasheet_en-gb.pdf | [36 empty] | 369 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
5566 | LH24A-MF300-TP | LH24A-MF300-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF300-TP_4C.jpg | LH24A-MF300-TP | LH24A-MF300-TP_datasheet_en-gb.pdf | [36 empty] | 367 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
69833 | CH24-L60 | CH24-L60.2 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | [5 empty] | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable through contact assignment |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH24-L60 | CH24-L60_datasheet_en-gb.pdf | [36 empty] | 303 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\Open-Close, 3-point\AC/DC 24 V\
4833 | LM24AP5 | LM24AP5 | AC/DC 24 V | 1 W | 0.2 W | 1.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24AP5_4C.jpg | LM24AP5 | LM24AP5_datasheet_en-gb.pdf | [36 empty] | 344 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
69836 | CM24-L-100D.2 | CM24-L-100D.2 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM24-L-100D | CM24-L-100D_datasheet_en-gb.pdf | [36 empty] | 315 | EU\Products\Air solutions\Internal actuators with damper\CM..D.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
4835 | LM24A | LM24A | AC/DC 24 V | 1 W | 0.2 W | 1.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A_4C.jpg | LM24A | LM24A_datasheet_en-gb.pdf | [36 empty] | 725 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
69829 | CH24-SR-R100 | CH24-SR-R100.2 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | cw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH24-SR-R100 | CH24-SR-R100_datasheet_en-gb.pdf | [36 empty] | 301 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
4841 | LM230ASR-TP | LM230ASR-TP | AC 230 V | 2 W | 1 W | 4 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM230ASR-TP_4C.jpg | LM230ASR-TP | LM230ASR-TP_datasheet_en-gb.pdf | [36 empty] | 379 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating\AC 230 V\
5574 | SM24A-MF | SM24A-MF | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MF_01_4C.jpg | SM24A-MF | SM24A-MF_datasheet_en-gb.pdf | [36 empty] | 413 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating, MF\AC/DC 24 V\
4839 | LM230A-TP | LM230A-TP | AC 230 V | 1.5 W | 0.5 W | 3.5 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM230A-TP_4C.jpg | LM230A-TP | LM230A-TP_datasheet_en-gb.pdf | [36 empty] | 345 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC 230 V\
5565 | LH24A-MF200-TP | LH24A-MF200-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF200-TP_4C.jpg | LH24A-MF200-TP | LH24A-MF200-TP_datasheet_en-gb.pdf | [36 empty] | 367 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
4843 | LM230A-S | LM230A-S | AC 230 V | 1.5 W | 0.5 W | 3.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM230A-S_4C.jpg | LM230A-S | LM230A-S_datasheet_en-gb.pdf | [36 empty] | 359 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC 230 V\
5561 | LH24A-MF300 | LH24A-MF300 | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MP300_4C.jpg | LH24A-MF300 | LH24A-MF300_datasheet_en-gb.pdf | [36 empty] | 365 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
69828 | CH24-SR-R60 | CH24-SR-R60.2 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | cw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH24-SR-R60 | CH24-SR-R60_datasheet_en-gb.pdf | [36 empty] | 300 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
69838 | CM24-L-150D.2 | CM24-L-150D.2 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM24-L-150D | CM24-L-150D_datasheet_en-gb.pdf | [36 empty] | 288 | EU\Produkte\Lüftungsanwendungen\Antriebe mit Klappenblatt\CM..D.. (2 Nm)\Auf-Zu, 3-Punkt\AC/DC 24 V\
5568 | LH24A-MP300 | LH24A-MP300 | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MP300_4C.jpg | LH24A-MP300 | LH24A-MP300_datasheet_en-gb.pdf | [36 empty] | 401 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MP\AC/DC 24 V\
5575 | LM24A-MP | LM24A-MP | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-MP_4C.jpg | LM24A-MP | LM24A-MP_datasheet_en-gb.pdf | [36 empty] | 421 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating, MP\AC/DC 24 V\
69831 | CH230-L100 | CH230-L100.2 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | [5 empty] | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable through contact assignment |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH230-L100 | CH230-L100_datasheet_en-gb.pdf | [36 empty] | 277 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\Open-Close, 3-point\AC 230 V\
4838 | LM72A | LM72A | DC 48...110 V | 2.5 W | 2 W | 2.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM72A_4C.jpg | LM72A | LM72A_datasheet_en-gb.pdf | [36 empty] | 366 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\DC 48...110 V\
4832 | LM24A-S | LM24A-S | AC/DC 24 V | 1 W | 0.2 W | 1.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-S_4C.jpg | LM24A-S | LM24A-S_datasheet_en-gb.pdf | [36 empty] | 423 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
69776 | NF24G-MP-L | NF24G-MP-L | AC/DC 24 V | 7 W | 3.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM..G-T-neutral_01_4C.jpg | NF24G-MP-L | NF24G-MP-L_datasheet_en-gb.pdf | [36 empty] | 369 | EU\Products\Air solutions\IP66/NEMA4 actuator\NF..G (10 Nm)\modulating, MP\AC/DC 24 V\
4840 | LM230A-S-TP | LM230A-S-TP | AC 230 V | 1.5 W | 0.5 W | 3.5 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM230A-S-TP_4C.jpg | LM230A-S-TP | LM230A-S-TP_datasheet_en-gb.pdf | [36 empty] | 352 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC 230 V\
5560 | LH24A-MF200 | LH24A-MF200 | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF200_4C.jpg | LH24A-MF200 | LH24A-MF200_datasheet_en-gb.pdf | [36 empty] | 357 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
5563 | LH24A-MF60-TP | LH24A-MF60-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF100-TP_4C.jpg | LH24A-MF60-TP | LH24A-MF60-TP_datasheet_en-gb.pdf | [36 empty] | 380 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MF\AC/DC 24 V\
4837 | LM24A-TP | LM24A-TP | AC/DC 24 V | 1 W | 0.2 W | 1.5 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-TP_4C.jpg | LM24A-TP | LM24A-TP_datasheet_en-gb.pdf | [36 empty] | 369 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
5567 | LH24A-MP200 | LH24A-MP200 | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MP-200_4C.jpg | LH24A-MP200 | LH24A-MP200_datasheet_en-gb.pdf | [36 empty] | 396 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MP\AC/DC 24 V\
4834 | LM24A-F | LM24A-F | AC/DC 24 V | 1 W | 0.2 W | 1.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_LM24A-F_4C.jpg | LM24A-F | LM24A-F_datasheet_en-gb.pdf | [36 empty] | 316 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC/DC 24 V\
5573 | LM24A-MF | LM24A-MF | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A_MF-neutral_01_4C.jpg | LM24A-MF | LM24A-MF_datasheet_en-gb.pdf | [36 empty] | 434 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating, MF\AC/DC 24 V\
4830 | LM24A-SR | LM24A-SR | AC/DC 24 V | 1 W | 0.4 W | 2 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-SR_4C.jpg | LM24A-SR | LM24A-SR_datasheet_en-gb.pdf | [36 empty] | 425 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating\AC/DC 24 V\
69830 | CH24-SR-L60 | CH24-SR-L60.2 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | ccw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH24-SR-L60 | CH24-SR-L60_datasheet_en-gb.pdf | [36 empty] | 320 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
4842 | LM230ASR | LM230ASR | AC 230 V | 2 W | 1 W | 4 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM230ASR_4C.jpg | LM230ASR | LM230ASR_datasheet_en-gb.pdf | [36 empty] | 405 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating\AC 230 V\
5562 | LH24A-MP100 | LH24A-MP100 | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MP100_4C.jpg | LH24A-MP100 | LH24A-MP100_datasheet_en-gb.pdf | [36 empty] | 408 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MP\AC/DC 24 V\
69853 | CM230-L-125D.2 | CM230-L-125D.2 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM230-L-125D | CM230-L-125D_datasheet_en-gb.pdf | [36 empty] | 285 | EU\Products\Air solutions\Internal actuators with damper\CM..D.. (2 Nm)\Open-Close, 3-point\AC 230 V\
4847 | LM72A-S | LM72A-S | DC 48...110 V | 2.5 W | 2 W | 2.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) | 1 x SPDT | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM72A-S_4C.jpg | LM72A-S | LM72A-S_datasheet_en-gb.pdf | [36 empty] | 322 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\DC 48...110 V\
5583 | NMC24A-MF | NMC24A-MF | AC/DC 24 V | 4 W | 1.5 W | 7 VA | Cable | 10 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NMC24A-MF_4C.jpg | NMC24A-MF | NMC24A-MF_datasheet_en-gb.pdf | [36 empty] | 336 | EU\Products\Air solutions\Fast runner actuators\NMC..A (10 Nm)\modulating, MF\AC/DC 24 V\
4844 | LM230A-F | LM230A-F | AC 230 V | 1.5 W | 0.5 W | 3.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_LM230A-F_4C.jpg | LM230A-F | LM230A-F_datasheet_en-gb.pdf | [36 empty] | 320 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC 230 V\
5586 | SM24A-PC | SM24A-PC | AC/DC 24 V | 3.5 W | 1.25 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating |  |  | DC 0...20 V Phase-cut signal | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MA-OR_4C.jpg | SM24A-PC | SM24A-PC_datasheet_en-gb.pdf | [36 empty] | 412 | EU\Products\Air solutions\Retrofit actuators\SM..A (20 Nm)\modulating\AC/DC 24 V\
5580 | LU24A-MF | LU24A-MF | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable | 3 Nm |  |  |  | 0...1800° | 150 s | 360° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Form fit 12 mm or 8 mm (with insert) | -30°C … 50°C |  | PIC_EU_LU24A-MF_4C.jpg | LU24A-MF | LU24A-MF_datasheet_en-gb.pdf | [36 empty] | 350 | EU\Products\Air solutions\Full-rotation actuators\LU..A (3 Nm)\modulating, MF\AC/DC 24 V\
61157 | Z-SMA | Z-SMA | [26 empty] | PIC_EU_Z-SMA_BW.jpg | Z-SMA | [37 empty] | 187 | EU\Products\Accessories\Mechanical accessories\Air solutions\Baseplate extension\
69850 | CM24-SR-L-150D.2 | CDA-030 S01 0202 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM24-SR-L-150D | CM24-SR-L-150D_datasheet_en-gb.pdf | [36 empty] | 300 | EU\Produkte\Lüftungsanwendungen\Antriebe mit Klappenblatt\CM..D.. (2 Nm)\stetig\AC/DC 24 V\
69855 | CM230-L-160D.2 | CDA-060 T01 0032 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM230-L-160D | CM230-L-160D_datasheet_en-gb.pdf | [36 empty] | 284 | EU\Products\Air solutions\Internal actuators with damper\CM..D.. (2 Nm)\Open-Close, 3-point\AC 230 V\
69863 | CH24-L100 | CH24-L100.2 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | [5 empty] | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable through contact assignment |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH24-L100 | CH24-L100_datasheet_en-gb.pdf | [36 empty] | 277 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\Open-Close, 3-point\AC/DC 24 V\
4849 | LH24A100 | LH24A100 | AC/DC 24 V | 1.5 W | 0.5 W | 3 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH24A100_4C.jpg | LH24A100 | LH24A100_datasheet_en-gb.pdf | [36 empty] | 323 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC/DC 24 V\
4852 | LH24A-SX60 | LH24A-SX60 | AC/DC 24 V | 2.5 W | 0.9 W | 4.5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-SX60_4C.jpg | LH24A-SX60 | LH24A-SX60_datasheet_en-gb.pdf | [36 empty] | 321 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating\AC/DC 24 V\
5582 | NM24P-MF | NM24P-MF | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 10...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NM24P-MF | NM24P_datasheet_en-gb.pdf | [36 empty] | 359 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\modulating, MF\AC/DC 24 V\
5585 | SM24A-MA | SM24A-MA | AC/DC 24 V | 3.5 W | 1.25 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | 0...20 mA |  | 4...20 mA | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MA-OR_4C.jpg | SM24A-MA | SM24A-MA_datasheet_en-gb.pdf | [36 empty] | 410 | EU\Products\Air solutions\Retrofit actuators\SM..A (20 Nm)\modulating\AC/DC 24 V\
69852 | CM230-L-100D.2 | CM230-L-100D.2 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM230-L-100D | CM230-L-100D_datasheet_en-gb.pdf | [36 empty] | 282 | EU\Produkte\Lüftungsanwendungen\Antriebe mit Klappenblatt\CM..D.. (2 Nm)\Auf-Zu, 3-Punkt\AC 230 V\
4858 | LH230A60 | LH230A60 | AC 230 V | 1.5 W | 1 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH24A-SX60_4C.jpg | LH230A60 | LH230A60_datasheet_en-gb.pdf | [36 empty] | 318 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC 230 V\
4851 | LH24A300 | LH24A300 | AC/DC 24 V | 1.5 W | 0.5 W | 3 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH24A300_4C.jpg | LH24A300 | LH24A300_datasheet_de-ch.pdf | [36 empty] | 321 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC/DC 24 V\
5579 | GM24A-MF | GM24A-MF | AC/DC 24 V | 4 W | 1.5 W | 7 VA | Cable | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-MF_4C.jpg | GM24A-MF | GM24A-MF_datasheet_en-gb.pdf | [36 empty] | 373 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\modulating, MF\AC/DC 24 V\
69847 | CM24-SR-L-100D.2 | CDA-030 P01 0202 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM24-SR-L-100D | CM24-SR-L-100D_datasheet_en-gb.pdf | [36 empty] | 297 | EU\Produkte\Lüftungsanwendungen\Antriebe mit Klappenblatt\CM..D.. (2 Nm)\stetig\AC/DC 24 V\
4854 | LH24A-SR200 | LH24A-SR200 | AC/DC 24 V | 1.5 W | 0.5 W | 3 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-SR200_4C.jpg | LH24A-SR200 | LH24A-SR200_datasheet_en-gb.pdf | [36 empty] | 354 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating\AC/DC 24 V\
5587 | SM24A-R9 | SM24A-R9 | AC/DC 24 V | 3.5 W | 1.25 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating |  |  | 0...135 Ω | DC 2...10 V | Cable 1 m, 5 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MA-OR_4C.jpg | SM24A-R9 | SM24A-R9_datasheet_en-gb.pdf | [36 empty] | 394 | EU\Products\Air solutions\Retrofit actuators\SM..A (20 Nm)\modulating\AC/DC 24 V\
69854 | CM230-L-150D.2 | CM230-L-150D.2 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM230-L-150D | CM230-L-150D_datasheet_en-gb.pdf | [36 empty] | 283 | EU\Products\Air solutions\Internal actuators with damper\CM..D.. (2 Nm)\Open-Close, 3-point\AC 230 V\
5577 | NM24A-MF | NM24A-MF | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-MF_01_4C.jpg | NM24A-MF | NM24A-MF_datasheet_en-gb.pdf | [36 empty] | 370 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating, MF\AC/DC 24 V\
4848 | LH24A60 | LH24A60 | AC/DC 24 V | 1.5 W | 0.5 W | 3 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH24A-SX60_4C.jpg | LH24A60 | LH24A60_datasheet_en-gb.pdf | [36 empty] | 330 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC/DC 24 V\
69839 | CM24-L-160D.2 | CDA-000 T01 0032 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM24-L-160D | CM24-L-160D_datasheet_en-gb.pdf | [36 empty] | 295 | EU\Produkte\Lüftungsanwendungen\Antriebe mit Klappenblatt\CM..D.. (2 Nm)\Auf-Zu, 3-Punkt\AC/DC 24 V\
5584 | SMC24A-MF | SMC24A-MF | AC/DC 24 V | 4 W | 1.5 W | 7 VA | Cable | 20 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 55 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SMC24A-MF_4C.jpg | SMC24A-MF | SMC24A-MF_datasheet_en-gb.pdf | [36 empty] | 374 | EU\Products\Air solutions\Fast runner actuators\SMC..A (20 Nm)\modulating, MF\AC/DC 24 V\
69867 | CH24-SR-L100 | CHA-L30 001 016 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  | 125 N |  |  | 380 s | 100 mm |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | ccw rotation |  |  | -30°C … 50°C |  | PIC_EU_CH24-L100_4C.jpg | CH24-SR-L100 | CH24-SR-L100_datasheet_en-gb.pdf | [36 empty] | 303 | EU\Products\Air solutions\Linear actuators\CH.. (125 N)\modulating\AC/DC 24 V\
5581 | LU24A-MP | LU24A-MP | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Cable | 3 Nm |  |  |  | 0...1800° | 150 s | 360° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Form fit 12 mm or 8 mm (with insert) | -30°C … 50°C |  | PIC_EU_LU24A-MP_4C.jpg | LU24A-MP | LU24A-MP_datasheet_en-gb.pdf | [36 empty] | 389 | EU\Products\Air solutions\Full-rotation actuators\LU..A (3 Nm)\modulating, MP\AC/DC 24 V\
4846 | LM72A-SR | LM72A-SR | DC 48...110 V | 2.5 W | 2 W | 2.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM72A-SR_4C.jpg | LM72A-SR | LM72A-SR_datasheet_en-gb.pdf | [36 empty] | 346 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating\DC 48...110 V\
69851 | CM24-SR-L-160D.2 | CDA-030 T01 0202 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM24-SR-L-160D | CM24-SR-L-160D_datasheet_en-gb.pdf | [36 empty] | 294 | EU\Produkte\Lüftungsanwendungen\Antriebe mit Klappenblatt\CM..D.. (2 Nm)\stetig\AC/DC 24 V\
5576 | SM24A-MP | SM24A-MP | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MP_4C.jpg | SM24A-MP | SM24A-MP_datasheet_en-gb.pdf | [36 empty] | 431 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\SM..A (20 Nm)\stetig, MP\AC/DC 24 V\
4850 | LH24A200 | LH24A200 | AC/DC 24 V | 1.5 W | 0.5 W | 3 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH24A200_4C.jpg | LH24A200 | LH24A200_datasheet_en-gb.pdf | [36 empty] | 311 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC/DC 24 V\
69849 | CM24-SR-L-125D.2 | CM24-SR-L-125D.2 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable |  |  |  |  | 70° | 58 s |  |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 |  |  |  | -30°C … 50°C |  | PIC_EU_CM..D-neutral24V_01_4C.jpg | CM24-SR-L-125D | CM24-SR-L-125D_datasheet_en-gb.pdf | [36 empty] | 295 | EU\Produkte\Lüftungsanwendungen\Antriebe mit Klappenblatt\CM..D.. (2 Nm)\stetig\AC/DC 24 V\
4853 | LH24A-SR100 | LH24A-SR100 | AC/DC 24 V | 1.5 W | 0.5 W | 3 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-SR100_4C.jpg | LH24A-SR100 | LH24A-SR100_datasheet_en-gb.pdf | [36 empty] | 341 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating\AC/DC 24 V\
286528 | GM24A-MOD | GM24A-MOD | AC/DC 24 V | 4 W | 1.6 W | 7 VA | Cable | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | communicative |  |  |  |  | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 12...26.7 mm | -30°C ... 50°C |  | PIC_EU_GM24A-MOD-neutral_4C.jpg | GM24A-MOD | GM24A-MOD_datasheet_en-gb.pdf | [36 empty] | 107 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\modulating, MOD\AC/DC 24 V\
4845 | LM230A | LM230A | AC 230 V | 1.5 W | 0.5 W | 3.5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM230A_4C.jpg | LM230A | LM230A_datasheet_en-gb.pdf | [36 empty] | 355 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\Open-Close, 3-point\AC 230 V\
5578 | GM24A-MP | GM24A-MP | AC/DC 24 V | 4 W | 1.6 W | 7 VA | Cable | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-MP_4C.jpg | GM24A-MP | GM24A-MP_datasheet_en-gb.pdf | [36 empty] | 393 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\GM..A (40 Nm)\stetig, MP\AC/DC 24 V\
99615 | SFA | SFA | AC 24...240 V / DC 24...125 V | 7 W | 3.5 W | 18 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF-1Kabel-neutral_01_4C.jpg | SFA | SFA_datasheet_en-gb.pdf | [36 empty] | 277 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\Open-Close, 3-point\AC 24...240V / DC 24...125V\
5589 | NM24ALON | NM24ALON | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | communicative |  |  |  | DC 2...10 V | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24ALON_4C.jpg | NM24ALON | SF24ALON_datasheet_en-gb.pdf | [36 empty] | 389 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating, LON\AC/DC 24 V\
99612 | NFA-S2 | NFA-S2 | AC 24...240 V / DC 24...125 V | 6 W | 2.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF-2Kabel-neutral_01_4C.jpg | NFA-S2 | NFA-S2_datasheet_en-gb.pdf | [36 empty] | 291 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\Open-Close\AC 24...240V / DC 24...125V\
5595 | NM24A-MF-TP | NM24A-MF-TP | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-MF-TP_4C.jpg | NM24A-MF-TP | NM24A-MF-TP_datasheet_en-gb.pdf | [36 empty] | 375 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating, MF\AC/DC 24 V\
4868 | SH24A200 | SH24A200 | AC/DC 24 V | 2 W | 0.2 W | 4.5 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_SH24A200_4C.jpg | SH24A200 | SH24A200_datasheet_en-gb.pdf | [36 empty] | 307 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\Open-Close, 3-point\AC/DC 24 V\
99614 | SFA-S2 | SFA-S2 | AC 24...240 V / DC 24...125 V | 7 W | 3.5 W | 18 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF24A-S2_4C.jpg | SFA-S2 | SFA-S2_datasheet_en-gb.pdf | [36 empty] | 291 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\Open-Close, 3-point\AC 24...240V / DC 24...125V\
4860 | LH230A200 | LH230A200 | AC 230 V | 1.5 W | 1 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH230A200_4C.jpg | LH230A200 | LH230A200_datasheet_en-gb.pdf | [36 empty] | 311 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC 230 V\
4870 | SH24A-SR100 | SH24A-SR100 | AC/DC 24 V | 2.5 W | 0.4 W | 4.5 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-SR100_4C.jpg | SH24A-SR100 | SH24A-SR100_datasheet_en-gb.pdf | [36 empty] | 316 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating\AC/DC 24 V\
5619 | NM24A-MP | NM24A-MP | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-MF_4C.jpg | NM24A-MP | NM24A-MP_datasheet_en-gb.pdf | [36 empty] | 395 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\NM..A (10 Nm)\stetig, MP\AC/DC 24 V\
4859 | LH230A100 | LH230A100 | AC 230 V | 1.5 W | 1 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH230A100_4C.jpg | LH230A100 | LH230A100_datasheet_en-gb.pdf | [36 empty] | 311 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC 230 V\
5594 | LM24A-MF-TP | LM24A-MF-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-MF-TP_4C.jpg | LM24A-MF-TP | LM24A-MF-TP_datasheet_en-gb.pdf | [36 empty] | 373 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating, MF\AC/DC 24 V\
5598 | SM24A-MP-TP | SM24A-MP-TP | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MP-TP_4C.jpg | SM24A-MP-TP | SM24A-MP-TP_datasheet_en-gb.pdf | [36 empty] | 440 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating, MP\AC/DC 24 V\
4864 | LH230ASR200 | LH230ASR200 | AC 230 V | 2.5 W | 1 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH230ASR200_4C.jpg | LH230ASR200 | LH230ASR200_datasheet_en-gb.pdf | [36 empty] | 358 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating\AC 230 V\
61278 | K-LU | K-LU | [26 empty] | PIC_EU_K-LU_Spindle clamp_BW.jpg | K-LU | [37 empty] | 193 | EU\Products\Accessories\Mechanical accessories\Air solutions\Spindle clamp\
4867 | SH24A100 | SH24A100 | AC/DC 24 V | 2 W | 0.2 W | 4.5 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_SH24A100_4C.jpg | SH24A100 | SH24A100_datasheet_en-gb.pdf | [36 empty] | 312 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\Open-Close, 3-point\AC/DC 24 V\
99617 | NKQ24A-SR | NKQ24A-SR | AC/DC 24 V | 11 W | 3 W | 22 VA | Cable | 6 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 4 s | 90° | 4 s / 90° | 60 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NKQ24A-MF-4c.jpg | NKQ24A-SR | NKQ24A-SR_datasheet_en-gb.pdf | [36 empty] | 286 | EU\Products\Air solutions\SuperCap actuators\NKQ..A (6 Nm)\modulating\AC/DC 24 V\
5590 | SM24ALON | SM24ALON | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | communicative |  |  |  | DC 2...10 V | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MF-neutral_01_4C.jpg | SM24ALON | SM24ALON_datasheet_en-gb.pdf | [36 empty] | 431 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating, LON\AC/DC 24 V\
5588 | LM24ALON | LM24ALON | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Cable | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | communicative |  |  |  | DC 2...10 V | Cable 1 m, 6 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24ALON_4C.jpg | LM24ALON | SF24ALON_datasheet_en-gb.pdf | [36 empty] | 377 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating, LON\AC/DC 24 V\
5597 | SM24A-MF-TP | SM24A-MF-TP | AC/DC 24 V | 3.5 W | 1.3 W | 6 VA | Terminals | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SM24A-MF-TP_4C.jpg | SM24A-MF-TP | SM24A-MF-TP_datasheet_en-gb.pdf | [36 empty] | 406 | EU\Products\Air solutions\Standard actuators\SM..A (20 Nm)\modulating, MF\AC/DC 24 V\
4861 | LH230A300 | LH230A300 | AC 230 V | 1.5 W | 1 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_LH230A300_4C.jpg | LH230A300 | LH230A300_datasheet_en-gb.pdf | [36 empty] | 302 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\Open-Close, 3-point\AC 230 V\
4869 | SH24A300 | SH24A300 | AC/DC 24 V | 2 W | 0.2 W | 4.5 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_SH24A300_4C.jpg | SH24A300 | SH24A300_datasheet_en-gb.pdf | [36 empty] | 307 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\Open-Close, 3-point\AC/DC 24 V\
4863 | LH230ASR100 | LH230ASR100 | AC 230 V | 2.5 W | 1 W | 5 VA | Cable |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH230ASR100_4C.jpg | LH230ASR100 | LH230ASR100_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating\AC 230 V\
99616 | SHK24A-SR100 | SHK24A-SR100 | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable |  |  | 450 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SHK24A-MP100_4C.jpg | SHK24A-SR100 | SHK24A-SR100_datasheet_en-gb.pdf | [36 empty] | 305 | EU\Products\Air solutions\SuperCap-Linear actuators\SHK..A (450 N)\modulating\AC/DC 24 V\
99613 | NFA | NFA | AC 24...240 V / DC 24...125 V | 6 W | 2.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF24A_4C.jpg | NFA | NFA_datasheet_en-gb.pdf | [36 empty] | 332 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\Open-Close\AC 24...240V / DC 24...125V\
4871 | SH24A-SR200 | SH24A-SR200 | AC/DC 24 V | 2.5 W | 0.4 W | 4.5 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH24A-SR200_4C.jpg | SH24A-SR200 | SH24A-SR200_datasheet_en-gb.pdf | [36 empty] | 341 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating\AC/DC 24 V\
5618 | SBG24 | SBG24 | AC 24 V | 1 W |  | 1.5 VA | Terminals |  |  |  |  | adjustable electron. min./max. angle of rotation limiting | [9 empty] | Terminals 4 mm² | IP40 | [5 empty] | PIC_EU_SBG24_4C.jpg | SBG24 | [37 empty] | 283 | EU\Products\Accessories\Electrical accessories\Positioner\
277728 | LH24A-MP60-TP | LH24A-MP60-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF100-TP_4C.jpg | LH24A-MP60-TP | LH24A-MP60-TP_datasheet_en-gb.pdf | [36 empty] | 154 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MP\AC/DC 24 V\
61439 | GM230G-T | GM230G-T | AC 230 V | 5 W | 2.5 W | 9 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP66 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_GM..G-T-neutral_01_4C.jpg | GM230G-T | GM230G-T_datasheet_en-gb.pdf | [36 empty] | 320 | EU\Products\Air solutions\IP66/NEMA4 actuator\GM..G-T (40 Nm)\Open-Close\AC 230 V\
99618 | NKQ24P-MF | NKQ24P-MF | AC/DC 24 V | 11 W | 3 W | 22 VA | Cable | 6 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 4 s | 90° | 4 s / 90° | 60 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NKQ24P-MF | NKQ24P-MF_datasheet_en-gb.pdf | [36 empty] | 332 | EU\Products\Air solutions\RobustLine actuators\NKQ..P (6 Nm)\modulating, MF\AC/DC 24 V\
99733 | SHK24A-MP100 | SHK24A-MP100 | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable |  |  | 450 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SHK24A-MP100_4C.jpg | SHK24A-MP100 | SHK24A-MP100_datasheet_en-gb.pdf | [36 empty] | 360 | EU\Products\Air solutions\SuperCap-Linear actuators\SHK..A (450 N)\modulating, MP\AC/DC 24 V\
61450 | GK24G-1 | GK24G-1 | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 52 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | GK24G-1 | GK24G-1_datasheet_en-gb.pdf | [36 empty] | 332 | EU\Products\Air solutions\IP66/NEMA4 actuator\GK..G (40 Nm)\Open-Close\AC/DC 24 V\
277730 | SMC24A-MP | SMC24A-MP | AC/DC 24 V | 4 W | 1.5 W | 7 VA | Cable | 20 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 55 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 10...20 mm | -30°C … 50°C |  | PIC_EU_SMC24A-MF_4C.jpg | SMC24A-MP | SMC24A-MP_datasheet_en-gb.pdf | [36 empty] | 133 | EU\Products\Air solutions\Fast runner actuators\SMC..A (20 Nm)\modulating, MF\AC/DC 24 V\
4877 | SH230ASR100 | SH230ASR100 | AC 230 V | 3 W | 1 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH230ASR100_4C.jpg | SH230ASR100 | SH230ASR100_datasheet_en-gb.pdf | [36 empty] | 328 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating\AC 230 V\
61445 | GM24G-MF-T | GM24G-MF-T | AC/DC 24 V | 4 W | 1.5 W | 7 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_GM..G-T-neutral_01_4C.jpg | GM24G-MF-T | GM24G-MF-T_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\IP66/NEMA4 actuator\GM..G-T (40 Nm)\modulating, MF\AC/DC 24 V\
99620 | NKQ24P-SR | NKQ24P-SR | AC/DC 24 V | 11 W | 3 W | 22 VA | Cable | 6 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 4 s | 90° | 4 s / 90° | 60 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NKQ24P-SR | NKQ24P-SR_datasheet_en-gb.pdf | [36 empty] | 307 | EU\Products\Air solutions\RobustLine actuators\NKQ..P (6 Nm)\modulating\AC/DC 24 V\
61424 | EF24A | EF24A | AC/DC 24 V | 9.5 W | 4.5 W | 16 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 56 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP54 | selectable by mounting L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_EF24A_4C.jpg | EF24A | EF24A_datasheet_en-gb.pdf | [36 empty] | 370 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\Open-Close\AC/DC 24 V\
61433 | EF230A | EF230A | AC 230 V | 9 W | 4.5 W | 21 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 56 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP54 | selectable by mounting L / R |  | Universal spindle clamp 12...26.7 mm |  |  | PIC_EU_EF230A_4C.jpg | EF230A | EF230A_datasheet_en-gb.pdf | [36 empty] | 340 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\Open-Close\AC 230 V\
4882 | CM24-R | CM24-R | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24_4C.jpg | CM24-R | CM24-R_datasheet_en-gb.pdf | [36 empty] | 337 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\CM.. (2 Nm)\Auf-Zu, 3-Punkt\AC/DC 24 V\
61438 | GM24G-T | GM24G-T | AC/DC 24 V | 4 W | 2 W | 6 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | Open-close |  |  |  |  | Terminals 4 mm² (cable Ø 4...10 mm, 3-wire) | IP66 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_GM..G-T-neutral_01_4C.jpg | GM24G-T | GM24G-T_datasheet_en-gb.pdf | [36 empty] | 329 | EU\Products\Air solutions\IP66/NEMA4 actuator\GM..G-T (40 Nm)\Open-Close\AC/DC 24 V\
4875 | SH230A200 | SH230A200 | AC 230 V | 3 W | 0.6 W | 7 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_SH230A200_4C.jpg | SH230A200 | SH230A100_datasheet_en-gb.pdf | [36 empty] | 296 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\Open-Close, 3-point\AC 230 V\
277729 | NF24A-MP | NF24A-MP | AC/DC 24 V | 7 W | 3.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF-Connector-neutral_01_4C.jpg | NF24A-MP | NF24A-MP_datasheet_en-gb.pdf | [36 empty] | 166 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\modulating, MP\AC/DC 24 V\
277734 | GK24G-MP | GK24G-MP | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 52 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | GK24G-MP | GK24G-MP_datasheet_en-gb.pdf | [36 empty] | 137 | EU\Products\Air solutions\IP66/NEMA4 actuator\GK..G (40 Nm)\modulating, MF\AC/DC 24 V\
4885 | CM24-F-T-R | CMA-2R0 F00 003 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Terminals | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (3-wire) | IP20 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM-F-T-neutral_01_4C.jpg | CM24-F-T-R | CM24-F-T-R_datasheet_en-gb.pdf | [36 empty] | 311 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
4881 | CM24-L | CM24-L | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24_4C.jpg | CM24-L | CM24-L_datasheet_en-gb.pdf | [36 empty] | 367 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
277732 | NM24P-MP | NM24P-MP | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 10...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NM24P-MP | NM24P-MP_datasheet_en-gb.pdf | [36 empty] | 134 | EU\Products\Air solutions\RobustLine actuators\NM..P (10 Nm)\modulating, MF\AC/DC 24 V\
61451 | GK24G-SR | GK24G-SR | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 52 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | GK24G-SR | GK24G-SR_datasheet_en-gb.pdf | [36 empty] | 356 | EU\Products\Air solutions\IP66/NEMA4 actuator\GK..G (40 Nm)\modulating\AC/DC 24 V\
4878 | SH230ASR200 | SH230ASR200 | AC 230 V | 3 W | 1 W | 6 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SH230ASR200_4C.jpg | SH230ASR200 | SH230ASR200_datasheet_en-gb.pdf | [36 empty] | 336 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\modulating\AC 230 V\
4883 | CM24-F-L | CM24-F-L | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM24-F-L | CM24-F-L_datasheet_en-gb.pdf | [36 empty] | 354 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
61440 | GM24G-SR-T | GM24G-SR-T | AC/DC 24 V | 4.5 W | 2 W | 6.5 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_GM..G-T-neutral_01_4C.jpg | GM24G-SR-T | GM24G-SR-T_datasheet_en-gb.pdf | [36 empty] | 325 | EU\Products\Air solutions\IP66/NEMA4 actuator\GM..G-T (40 Nm)\modulating\AC/DC 24 V\
99619 | NKQ24P-1 | NKQ24P-1 | AC/DC 24 V | 11 W | 3 W | 22 VA | Cable | 6 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 4 s | 90° | 4 s / 90° | 60 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | NKQ24P-1 | NKQ24P-1_datasheet_en-gb.pdf | [36 empty] | 265 | EU\Products\Air solutions\RobustLine actuators\NKQ..P (6 Nm)\Open-Close, 3-point\AC/DC 24 V\
61426 | EF24A-SR | EF24A-SR | AC/DC 24 V | 7 W | 4.5 W | 12 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP54 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_EF24A-SR_4C.jpg | EF24A-SR | EF24A-SR_datasheet_en-gb.pdf | [36 empty] | 363 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\modulating\AC/DC 24 V\
61434 | EF230A-S2 | EF230A-S2 | AC 230 V | 9 W | 4.5 W | 21 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 56 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 12...26.7 mm |  |  | PIC_EU_EF230A-S2_4C.jpg | EF230A-S2 | EF230A-S2_datasheet_en-gb.pdf | [36 empty] | 346 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\Open-Close\AC 230 V\
99732 | SF24G-MP-L | SF24G-MP-L | AC/DC 24 V | 8.5 W | 3.5 W | 11 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM..G-T-neutral_01_4C.jpg | SF24G-MP-L | SF24G-MP-L_datasheet_en-gb.pdf | [36 empty] | 337 | EU\Products\Air solutions\IP66/NEMA4 actuator\SF..G (20 Nm)\modulating, MP\AC/DC 24 V\
61431 | EF24A-MF | EF24A-MF | AC/DC 24 V | 9.5 W | 4.5 W | 16 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP54 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_EF24A-MF_4C.jpg | EF24A-MF | EF24A-MF_datasheet_en-gb.pdf | [36 empty] | 410 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\modulating, MF\AC/DC 24 V\
4874 | SH230A100 | SH230A100 | AC 230 V | 3 W | 0.6 W | 7 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_SH230A100_4C.jpg | SH230A100 | SH230A100_datasheet_en-gb.pdf | [36 empty] | 301 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\Open-Close, 3-point\AC 230 V\
4876 | SH230A300 | SH230A300 | AC 230 V | 3 W | 0.6 W | 7 VA | Cable |  |  | 450 N |  |  | 150 s | 100 mm |  | 52 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (extended) / 1 (retracted) |  |  | -30°C … 50°C |  | PIC_EU_SH230A300_4C.jpg | SH230A300 | SH230A100_datasheet_en-gb.pdf | [36 empty] | 293 | EU\Products\Air solutions\Linear actuators\SH..A (450 N)\Open-Close, 3-point\AC 230 V\
277731 | NMC24A-MP | NMC24A-MP | AC/DC 24 V | 4 W | 1.5 W | 7 VA | Cable | 10 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NMC24A-MF_4C.jpg | NMC24A-MP | NMC24A-MP_datasheet_en-gb.pdf | [36 empty] | 151 | EU\Products\Air solutions\Fast runner actuators\NMC..A (10 Nm)\modulating, MF\AC/DC 24 V\
61427 | EF24A-SR-S2 | EF24A-SR-S2 | AC/DC 24 V | 7 W | 4.5 W | 12 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 45 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP54 | selectable with switch L / R | 2 x SPDT | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_EF24A-SR-S2_4C.jpg | EF24A-SR-S2 | EF24A-SR-S2_datasheet_en-gb.pdf | [36 empty] | 412 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\modulating\AC/DC 24 V\
61425 | EF24A-S2 | EF24A-S2 | AC/DC 24 V | 9.5 W | 4.5 W | 16 VA | Cable | 30 Nm | 30 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 56 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP54 | selectable by mounting L / R | 2 x SPDT | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_EF24A-S2_4C.jpg | EF24A-S2 | EF24A-S2_datasheet_en-gb.pdf | [36 empty] | 370 | EU\Products\Air solutions\Spring return actuators\EF..A (30 Nm)\Open-Close\AC/DC 24 V\
277733 | SM24P-MP | SM24P-MP | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Cable | 20 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 + IP67 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...20 mm | -30°C … 50°C |  | PIC_EU_Robustline-Luft-oFenster_01_4C.jpg | SM24P-MP | NM24P-MP_datasheet_en-gb.pdf | [36 empty] | 132 | EU\Products\Air solutions\RobustLine actuators\SM..P (20 Nm)\modulating, MF\AC/DC 24 V\
4889 | CM24G-SR-R | CM24G-SR-R | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP66 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SR-L_4C.jpg | CM24G-SR-R | CM24G-SR-R_datasheet_en-gb.pdf | [36 empty] | 344 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\CM.. (2 Nm)\stetig\AC/DC 24 V\
4894 | CM24-SR-L | CM24-SR-L | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SR-L_4C.jpg | CM24-SR-L | CM24-SR-L_datasheet_en-gb.pdf | [36 empty] | 337 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
4886 | CM24G-L | CM24G-L | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24_4C.jpg | CM24G-L | CM24G-L_datasheet_en-gb.pdf | [36 empty] | 330 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
100386 | GK24A-MP | GK24A-MP | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 52 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C ... 50°C |  | PIC_EU_GK24A-MF_01_4C.jpg | GK24A-MP | GK24A-MP_datasheet_en-gb.pdf | [36 empty] | 349 | EU\Products\Air solutions\SuperCap actuators\GK..A (40 Nm)\modulating, MP\AC/DC 24 V\
61482 | NFG-L | NFG-L | AC 24...240 V / DC 24...125 V | 6 W | 2.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP66 |  |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | NFG-L | NFG-L_datasheet_en-gb.pdf | [36 empty] | 338 | EU\Products\Air solutions\IP66/NEMA4 actuator\NF..G (10 Nm)\Open-Close\AC 24...240V / DC 24...125V\
61464 | SF24G-SR-S2-L | SF24G-SR-S2-L | AC/DC 24 V | 5 W | 3 W | 7 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R | 2 x SPDT | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-2cable-neutral_01_4C.jpg | SF24G-SR-S2-L | SF24G-SR-S2-L_datasheet_en-gb.pdf | [36 empty] | 339 | EU\Products\Air solutions\IP66/NEMA4 actuator\SF..G (20 Nm)\modulating\AC/DC 24 V\
61479 | NF24G-SR-S2-L | NF24G-SR-S2-L | AC/DC 24 V | 3.5 W | 2.5 W | 5.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R | 2 x SPDT | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-2cable-neutral_01_4C.jpg | NF24G-SR-S2-L | NF24G-SR-S2-L_datasheet_en-gb.pdf | [36 empty] | 333 | EU\Products\Air solutions\IP66/NEMA4 actuator\NF..G (10 Nm)\modulating\AC/DC 24 V\
6492 | CM24-F-R | CMA-2R0 F01 003 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM24-F-R | CM24-F-R_datasheet_en-gb.pdf | [36 empty] | 229 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
277815 | LH24A-MP200-TP | LH24A-MP200-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF200-TP_4C.jpg | LH24A-MP200-TP | LH24A-MP200-TP_datasheet_en-gb.pdf | [36 empty] | 147 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MP\AC/DC 24 V\
61454 | SMQ24G | SMQ24G | AC/DC 24 V | 15 W | 2 W | 26 VA | Cable | 16 Nm |  |  |  | Max. 95° | 7 s | 90° |  | 63 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² (halogen-free) | IP66 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 12...26.7 mm | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | SMQ24G | SMQ24G_datasheet_en-gb.pdf | [36 empty] | 316 | EU\Products\Air solutions\IP66/NEMA4 actuator\SMQ..G (16 Nm)\Open-Close\AC/DC 24 V\
4891 | CM24G-SR-F-R | CMA-2A0 F01 007 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP66 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM24-F-neutral_01_4C.jpg | CM24G-SR-F-R | CM24G-SR-F-R_datasheet_en-gb.pdf | [36 empty] | 337 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
4888 | CM24G-SR-L | CM24G-SR-L | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP66 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SR-L_4C.jpg | CM24G-SR-L | CM24G-SR-L_datasheet_en-gb.pdf | [36 empty] | 340 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
61481 | NF24G-SR-L | NF24G-SR-L | AC/DC 24 V | 3.5 W | 2.5 W | 5.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | NF24G-SR-L | NF24G-SR-L_datasheet_en-gb.pdf | [36 empty] | 332 | EU\Products\Air solutions\IP66/NEMA4 actuator\NF..G (10 Nm)\modulating\AC/DC 24 V\
4898 | CM24-SR-F-L | CM24-SR-F-L | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM24-SR-F-L | CM24-SR-F-L_datasheet_en-gb.pdf | [36 empty] | 329 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
61478 | NFG-S2-L | NFG-S2-L | AC 24...240 V / DC 24...125 V | 6 W | 2.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP66 |  | 2 x SPDT | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-2cable-neutral_01_4C.jpg | NFG-S2-L | NFG-S2-L_datasheet_en-gb.pdf | [36 empty] | 343 | EU\Products\Air solutions\IP66/NEMA4 actuator\NF..G (10 Nm)\Open-Close\AC 24...240V / DC 24...125V\
61466 | SF24G-MF-L | SF24G-MF-L | AC/DC 24 V | 8.5 W | 3.5 W | 11 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | SF24G-MF-L | SF24G-MF-L_datasheet_en-gb.pdf | [36 empty] | 380 | EU\Products\Air solutions\IP66/NEMA4 actuator\SF..G (20 Nm)\modulating, MF\
277814 | LH24A-MP100-TP | LH24A-MP100-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF100-TP_4C.jpg | LH24A-MP100-TP | LH24A-MP100-TP_datasheet_en-gb.pdf | [36 empty] | 149 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MP\AC/DC 24 V\
61456 | SMQ24G-MF | SMQ24G-MF | AC/DC 24 V | 15 W | 2 W | 26 VA | Cable | 16 Nm |  |  |  | Max. 95° | 7 s | 90° |  | 63 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 12...26.7 mm | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | SMQ24G-MF | SMQ24G-MF_datasheet_en-gb.pdf | [36 empty] | 344 | EU\Products\Air solutions\IP66/NEMA4 actuator\SMQ..G (16 Nm)\modulating, MF\AC/DC 24 V\
61489 | GM24A-MF-TP | GM24A-MF-TP | AC/DC 24 V | 4 W | 1.5 W | 7 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-MF-TP_4C.jpg | GM24A-MF-TP | [37 empty] | 369 | EU\Products\Air solutions\Standard actuators\GM..A (40 Nm)\modulating, MF\AC/DC 24 V\
4890 | CM24G-SR-F-L | CMA-2A0 F01 008 | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP66 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM24-F-neutral_01_4C.jpg | CM24G-SR-F-L | CM24G-SR-F-L_datasheet_en-gb.pdf | [36 empty] | 337 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
4887 | CM24G-R | CM24G-R | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24_4C.jpg | CM24G-R | CM24G-R_datasheet_en-gb.pdf | [36 empty] | 327 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
4895 | CM24-SR-R | CM24-SR-R | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SR-R_4C.jpg | CM24-SR-R | CM24-SR-R_datasheet_en-gb.pdf | [36 empty] | 333 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
61465 | SFG-S2-L | SFG-S2-L | AC 24...240 V / DC 24...125 V | 7 W | 3.5 W | 18 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP66 |  | 2 x SPDT | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-2cable-neutral_01_4C.jpg | SFG-S2-L | SFG-S2-L_datasheet_en-gb.pdf | [36 empty] | 333 | EU\Products\Air solutions\IP66/NEMA4 actuator\SF..G (20 Nm)\Open-Close\AC 24...240V / DC 24...125V\
61455 | SMQ24G-SR | SMQ24G-SR | AC/DC 24 V | 15 W | 2 W | 26 VA | Cable | 16 Nm |  |  |  | Max. 95° | 7 s | 90° |  | 63 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 12...26.7 mm | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | SMQ24G-SR | SMQ24G-SR_datasheet_en-gb.pdf | [36 empty] | 316 | EU\Products\Air solutions\IP66/NEMA4 actuator\SMQ..G (16 Nm)\modulating\AC/DC 24 V\
277816 | LH24A-MP300-TP | LH24A-MP300-TP | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Terminals |  |  | 150 N |  |  | 150 s | 100 mm |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_LH24A-MF300-TP_4C.jpg | LH24A-MP300-TP | LH24A-MP300-TP_datasheet_en-gb.pdf | [36 empty] | 143 | EU\Products\Air solutions\Linear actuators\LH..A (150 N)\modulating, MP\AC/DC 24 V\
61480 | NF24G-MF-L | NF24G-MF-L | AC/DC 24 V | 7 W | 3.5 W | 9.5 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | NF24G-MF-L | NF24G-MF-L_datasheet_en-gb.pdf | [36 empty] | 363 | EU\Products\Air solutions\IP66/NEMA4 actuator\NF..G (10 Nm)\modulating, MF\AC/DC 24 V\
61467 | SFG-L | SFG-L | AC 24...240 V / DC 24...125 V | 7 W | 3.5 W | 18 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 75 s | 90° | <20 s / 90° | 45 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² (halogen-free) | IP66 |  |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | SFG-L | SFG-L_datasheet_en-gb.pdf | [36 empty] | 338 | EU\Products\Air solutions\IP66/NEMA4 actuator\SF..G (20 Nm)\Open-Close\AC 24...240V / DC 24...125V\
4912 | CM230-F-L | CM230-F-L | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM230-F-L | CM230-F-L_datasheet_en-gb.pdf | [36 empty] | 302 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC 230 V\
4905 | CM24-T-R | CM24-T-R | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Terminals | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (3-wire) | IP20 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-T_4C.jpg | CM24-T-R | CM24-T-R_datasheet_en-gb.pdf | [36 empty] | 325 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
61493 | SHK24A-1-100 | SHK24A-1-100 | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable |  |  | 450 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (retracted) / 1 (extended) |  |  | -30°C … 50°C |  | PIC_EU_SHK24A-MP100_4C.jpg | SHK24A-1-100 | SHK24A-1-100_datasheet_en-gb.pdf | [36 empty] | 334 | EU\Products\Air solutions\SuperCap-Linear actuators\SHK..A (450 N)\Open-Close, 3-point\AC/DC 24 V\
4914 | CM230G-L | CM230G-L | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM230_4C.jpg | CM230G-L | CM230G-L_datasheet_en-gb.pdf | [36 empty] | 322 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC 230 V\
4907 | CM230-R | CM230-R | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM230_4C.jpg | CM230-R | CM230-R_datasheet_en-gb.pdf | [36 empty] | 325 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC 230 V\
4902 | CM24-SR-T-L | CM24-SR-T-L | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Terminals | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (4-wire) | IP20 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SR-T-L_4C.jpg | CM24-SR-T-L | CM24-SR-T-L_datasheet_en-gb.pdf | [36 empty] | 343 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
61505 | NKQ24A-SZ | NKQ24A-SZ | AC/DC 24 V | 11 W | 3 W | 22 VA | Cable | 6 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 4 s | 90° | 4 s / 90° | 60 dB(A) | modulating | DC 0...10 V |  | DC 0.5...10 V | DC 0.5...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NKQ24A-MF-4c.jpg | NKQ24A-SZ | NKQ24A-SZ_datasheet_en-gb.pdf | [36 empty] | 348 | EU\Products\Air solutions\SuperCap actuators\NKQ..A (6 Nm)\modulating\AC/DC 24 V\
61552 | SF24G-SR-L | SF24G-SR-L | AC/DC 24 V | 5 W | 3 W | 7 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch L / R |  | Universal spindle clamp 12...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | SF24G-SR-L | SF24G-SR-L_datasheet_en-gb.pdf | [36 empty] | 313 | EU\Products\Air solutions\IP66/NEMA4 actuator\SF..G (20 Nm)\modulating\AC/DC 24 V\
61503 | GK24G-MF | GK24G-MF | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 52 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² (halogen-free) | IP66 | selectable with switch 0 / 1 |  | Universal spindle clamp 14...26.7 mm | -30°C … 50°C |  | PIC_EU_IP66-NEMA4-1cable-neutral_01_4C.jpg | GK24G-MF | GK24G-MF_datasheet_en-gb.pdf | [36 empty] | 371 | EU\Products\Air solutions\IP66/NEMA4 actuator\GK..G (40 Nm)\modulating, MF\AC/DC 24 V\
61495 | NKQ24A-MF | NKQ24A-MF | AC/DC 24 V | 11 W | 3 W | 22 VA | Cable | 6 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 4 s | 90° | 4 s / 90° | 60 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NKQ24A-MF-4c.jpg | NKQ24A-MF | NKQ24A-MF_datasheet_en-gb.pdf | [36 empty] | 399 | EU\Products\Air solutions\SuperCap actuators\NKQ..A (6 Nm)\modulating, MF\
4899 | CM24-SR-F-R | CM24-SR-F-R | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Cable | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM24-SR-F-R | CM24-SR-F-R_datasheet_en-gb.pdf | [36 empty] | 324 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
4904 | CM24-T-L | CM24-T-L | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Terminals | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (3-wire) | IP20 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-T_4C.jpg | CM24-T-L | CM24-T-L_datasheet_en-gb.pdf | [36 empty] | 330 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
61490 | TMC230ASR | TMC230ASR | AC 230 V | 2 W | 1 W | 3.5 VA | Cable | 2 Nm |  |  |  | Max. 95° | 35 s | 90° |  | 40 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V |  | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_TMC230ASR_4C.jpg | TMC230ASR | TMC230ASR_datasheet_en-gb.pdf | [36 empty] | 324 | EU\Products\Air solutions\Fast runner actuators\TMC..A (2 Nm)\modulating\AC 230 V\
4901 | CM24-SR-F-T-R | CM24-SR-F-T-R | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Terminals | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (4-wire) | IP20 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM-F-T-neutral_01_4C.jpg | CM24-SR-F-T-R | CM24-SR-F-T-R_datasheet_en-gb.pdf | [36 empty] | 312 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\CM.. (2 Nm)\stetig\AC/DC 24 V\
4915 | CM230G-R | CM230G-R | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM230_4C.jpg | CM230G-R | CM230G-R_datasheet_en-gb.pdf | [36 empty] | 317 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC 230 V\
4906 | CM230-L | CM230-L | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | ccw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM230_4C.jpg | CM230-L | CM230-L_datasheet_en-gb.pdf | [36 empty] | 323 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC 230 V\
4913 | CM230-F-R | CM230-F-R | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM230-F-R | CM230-F-R_datasheet_en-gb.pdf | [36 empty] | 294 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC 230 V\
61494 | SHK24A-MF100 | SHK24A-MF100 | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable |  |  | 450 N | With electrical emergency control function 0...100% |  | 120 s | 100 mm | 35 s / 100 mm | 52 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 50°C |  | PIC_EU_SHK24A-MP100_4C.jpg | SHK24A-MF100 | SHK24A-MF100_datasheet_en-gb.pdf | [36 empty] | 393 | EU\Products\Air solutions\SuperCap-Linear actuators\SHK..A (450 N)\modulating, MF\AC/DC 24 V\
4903 | CM24-SR-T-R | CM24-SR-T-R | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Terminals | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (4-wire) | IP20 | cw rotation |  | Universal spindle clamp 6...12.7 mm | -30°C … 50°C |  | PIC_EU_CM24-SR-T-L_4C.jpg | CM24-SR-T-R | CM24-SR-T-R_datasheet_en-gb.pdf | [36 empty] | 340 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
4900 | CM24-SR-F-T-L | CM24-SR-F-T-L | AC/DC 24 V | 1 W | 0.5 W | 1.5 VA | Terminals | 2 Nm |  |  |  | 95°, fixed setting | 75 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (4-wire) | IP20 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM-F-T-neutral_01_4C.jpg | CM24-SR-F-T-L | CM24-SR-F-T-L_datasheet_en-gb.pdf | [36 empty] | 315 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\modulating\AC/DC 24 V\
61496 | NKQ24A-1 | NKQ24A-1 | AC/DC 24 V | 11 W | 3 W | 22 VA | Cable | 6 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 4 s | 90° | 4 s / 90° | 60 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (ccw rotation) / 1 (cw rotation) |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NKQ24A-MF-4c.jpg | NKQ24A-1 | NKQ24A-1_datasheet_en-gb.pdf | [36 empty] | 342 | EU\Products\Air solutions\SuperCap actuators\NKQ..A (6 Nm)\Open-Close\AC/DC 24 V\
4917 | CM230G-F-R | CMA-3U0 F01 003 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-F-neutral_01_4C.jpg | CM230G-F-R | CM230G-F-R_datasheet_en-gb.pdf | [36 empty] | 253 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\CM.. (2 Nm)\Auf-Zu, 3-Punkt\AC 230 V\
4923 | LHQ24A100 | LHQ24A100 | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable |  |  | 100 N |  |  | 3.5 s | 100 mm |  | 56 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (retracted) / 1 (extended) |  |  | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_LHQ24A100_4C.jpg | LHQ24A100 | LHQ24A100_datasheet_en-gb.pdf | [36 empty] | 318 | EU\Products\Air solutions\(Very)fast running linear actuators\LHQ..A (100 N)\Open-Close\AC/DC 24 V\
59894 | LF24-MFT2 | LF24-MFT2 | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 30 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 8...16 mm | -30°C … 50°C |  | PIC_EU_LF24_4C.jpg | LF24-MFT2 | LF24-MFT2_datasheet_en-gb.pdf | [36 empty] | 392 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\modulating, MF\AC/DC 24 V\
4916 | CM230G-F-L | CMA-2J0 F01 003 | AC 230 V | 1.5 W | 1 W | 3 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-F-neutral_01_4C.jpg | CM230G-F-L | CM230G-F-L_datasheet_en-gb.pdf | [36 empty] | 257 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC 230 V\
4919 | SHQ24A-MF100 | SHQ24A-MF100 | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable |  |  | 200 N |  |  | 7 s | 100 mm |  | 56 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_SHQ24A-MF100_4C.jpg | SHQ24A-MF100 | SHQ24A-MF100_datasheet_en-gb.pdf | [36 empty] | 359 | EU\Products\Air solutions\(Very)fast running linear actuators\SHQ..A (200 N)\modulating, MF\AC/DC 24 V\
61594 | GK24A-SZ | GKA-6L0 201 AE1 | AC/DC 24 V | 11 W | 3 W | 21 VA | Cable | 40 Nm |  |  | With electrical emergency control function 0...100% | Max. 95° | 150 s | 90° | 35 s / 90° | 52 dB(A) | modulating | DC 0...10 V |  | DC 0.5...10 V | DC 0.5...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GK24A-MF_01_4C.jpg | GK24A-SZ | GK24A-SZ_datasheet_en-gb.pdf | [36 empty] | 334 | EU\Products\Air solutions\SuperCap actuators\GK..A (40 Nm)\modulating\AC/DC 24 V\
303874 | CM24G-F-R | CMA-3R0 F01 003 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | cw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM24G-F-R | CM24G-F-R_datasheet_en-gb.pdf | [36 empty] | 35 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
59746 | S2A-F | S2A-F |  |  |  |  | Cable | [15 empty] | IP54 |  | 2 x SPDT |  | -30°C … 50°C |  | PIC_EU_S2A-F_4C.jpg | S2A-F | S2A-F_datasheet_en-gb.pdf | [36 empty] | 290 | EU\Products\Accessories\Electrical accessories\Auxiliary switch\
4918 | SHQ24A100 | SHQ24A100 | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable |  |  | 200 N |  |  | 7 s | 100 mm |  | 56 dB(A) | Open-close |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP54 | selectable with switch 0 (retracted) / 1 (extended) |  |  | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_SHQ24A100_4C.jpg | SHQ24A100 | SHQ24A100_datasheet_en-gb.pdf | [36 empty] | 316 | EU\Products\Air solutions\(Very)fast running linear actuators\SHQ..A (200 N)\Open-Close\AC/DC 24 V\
59893 | LF24-MFT | LF24-MFT | AC/DC 24 V | 2.5 W | 1.2 W | 5 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 30 dB(A) | modulating | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 8...16 mm |  |  | PIC_EU_LF24-MFT_01_4C.jpg | LF24-MFT | LF24-MFT_datasheet_en-gb.pdf | [36 empty] | 380 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\modulating, MF\AC/DC 24 V\
4924 | LHQ24A-MF100 | LHQ24A-MF100 | AC/DC 24 V | 13 W | 2 W | 23 VA | Cable |  |  | 100 N |  |  | 3.5 s | 100 mm |  | 56 dB(A) | modulating | DC 0...10 V | Open-close¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch |  |  | -30°C … 40°C Caution: +40...+50°C utilisation possible only under certain restrictions. Please contact your supplier. |  | PIC_EU_LHQ24A-MF100_4C.jpg | LHQ24A-MF100 | LHQ24A-MF100_datasheet_en-gb.pdf | [36 empty] | 361 | EU\Products\Air solutions\(Very)fast running linear actuators\LHQ..A (100 N)\modulating, MF\AC/DC 24 V\
303873 | CM24G-F-L | CMA-2L0 F01 003 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Cable | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Cable 1 m, 3 x 0.75 mm² | IP66 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM230-1-F_4C.jpg | CM24G-F-L | CM24G-F-L_datasheet_en-gb.pdf | [36 empty] | 38 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
59892 | LF24 | LF24 | AC/DC 24 V | 5 W | 2.5 W | 7 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 40...75 s | 90° | <20 s / 90° | 50 dB(A) | Open-close |  |  |  |  | Cable 1 m, 2 x 0.75 mm² | IP54 | selectable by mounting L / R |  | Universal spindle clamp 8...16 mm | -30°C ... 50°C |  | PIC_EU_LF24_4C.jpg | LF24 | LF24_datasheet_en-gb.pdf | [36 empty] | 391 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\Open-Close\AC/DC 24 V\
305110 | SF24A-3 | SF24A-3 | AC 24 V | 7.5 W | 2.5 W | 10 VA | Cable | 20 Nm | 20 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | 3-point |  |  |  |  | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_SF24A_4C.jpg | SF24A-3 | SF24A-3_datasheet_en-gb.pdf | [36 empty] | 24 | EU\Products\Air solutions\Spring return actuators\SF..A (20 Nm)\Open-Close, 3-point\AC/DC 24 V\
275871 | NM24A-SR-F | NM24A-SR-F | AC/DC 24 V | 2 W | 0.4 W | 4 VA | Cable | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating | DC 0...10 V |  | DC 2...10 V | DC 2...10 V | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch 0 / 1 |  | Form fit 8x8 mm |  |  | PIC_EU_NM24A-SR 040F_4C.jpg | NM24A-SR-F | Z-NM..A_datasheet_en-gb.pdf | [36 empty] | 139 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating\AC/DC 24 V\
277726 | GM24A-MP-TP | GM24A-MP-TP | AC/DC 24 V | 4 W | 1.6 W | 7 VA | Terminals | 40 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 45 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp reversible 12...26.7 mm | -30°C … 50°C |  | PIC_EU_GM24A-MF-TP_4C.jpg | GM24A-MP-TP | GM24A-MP-TP_datasheet_en-gb.pdf | [36 empty] | 141 | EU\Produkte\Lüftungsanwendungen\Standardantriebe\GM..A (40 Nm)\stetig, MP\AC/DC 24 V\
305109 | NF24A-3 | NF24A-3 | AC 24 V | 6.5 W | 2.5 W | 9 VA | Cable | 10 Nm | 10 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 40 dB(A) | 3-point |  |  |  |  | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 10...25.4 mm | -30°C … 50°C |  | PIC_EU_NF24A_4C.jpg | NF24A-3 | NF24A-3_datasheet_en-gb.pdf | [36 empty] | 26 | EU\Products\Air solutions\Spring return actuators\NF..A (10 Nm)\Open-Close\AC/DC 24 V\
4884 | CM24-F-T-L | CMA-000 F00 003 | AC/DC 24 V | 0.5 W | 0.2 W | 1 VA | Terminals | 2 Nm |  |  |  | 0...287.5°, | 75 s | 90° |  | 35 dB(A) | Open-close¦3-point |  |  |  |  | Terminals 1.5 mm² Cu wire or 1.0 mm² Cu strands (3-wire) | IP20 | ccw rotation |  | Form fit 8x8 mm | -30°C … 50°C |  | PIC_EU_CM-F-T-neutral_01_4C.jpg | CM24-F-T-L | [37 empty] | 329 | EU\Products\Air solutions\Standard actuators\CM.. (2 Nm)\Open-Close, 3-point\AC/DC 24 V\
304486 | LF24-3 | LF24-3 | AC/DC 24 V | 2.5 W | 2.5 W | 5 VA | Cable | 4 Nm | 4 Nm |  | With mechanical emergency control function | Max. 95° | 150 s | 90° | <20 s / 90° | 30 dB(A) | 3-point |  |  |  |  | Cable 1 m, 4 x 0.75 mm² | IP54 | selectable with switch L / R |  | Universal spindle clamp 8...16 mm | -30°C ... 50°C |  | PIC_EU_LF24-3_4C.jpg | LF24-3 | LF24-3_datasheet_en-gb.pdf | [36 empty] | 50 | EU\Products\Air solutions\Spring return actuators\LF.. (4 Nm)\Open-Close\AC/DC 24 V\
277725 | LM24A-MP-TP | LM24A-MP-TP | AC/DC 24 V | 2.5 W | 1.3 W | 5 VA | Terminals | 5 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 6...20 mm | -30°C … 50°C |  | PIC_EU_LM24A-MF-TP_4C.jpg | LM24A-MP-TP | LM24A-MP-TP_datasheet_en-gb.pdf | [36 empty] | 138 | EU\Products\Air solutions\Standard actuators\LM..A (5 Nm)\modulating, MP\AC/DC 24 V\
277727 | NM24A-MP-TP | NM24A-MP-TP | AC/DC 24 V | 3.5 W | 1.4 W | 6 VA | Terminals | 10 Nm |  |  |  | Max. 95° | 150 s | 90° |  | 35 dB(A) | modulating¦communicative | DC 0...10 V | Open-close¦3-point (AC only)¦Modulating (DC 0...32 V) | DC 2...10 V | DC 2...10 V | Terminals 4 mm² (cable Ø 4...10 mm, 4-wire) | IP54 | selectable with switch 0 / 1 |  | Universal spindle clamp 8...26.7 mm | -30°C … 50°C |  | PIC_EU_NM24A-MP-TP_4C.jpg | NM24A-MP-TP | NM24A-MP-TP_datasheet_en-gb.pdf | [36 empty] | 134 | EU\Products\Air solutions\Standard actuators\NM..A (10 Nm)\modulating, MP\AC/DC 24 V\
305313 | ZR-IF01: Only available at www.djadun.de | [66 empty] | 8 | EU\Competitors valves retrofit\Air solution\Djadun\