## Worksheet 0
PdmarticleID | Label | Product family | Product family short | Product type | Medium temperature | Control | Operating range Y | Communication | Emergency setting position (POP) deenergised | Running time motor | Actuating time motor | Actuating force | Auxiliary switch | Nominal voltage | Nominal torque | Degree of protection IEC/EN | Data sheet name | Data sheet PDF | 3432 | Product picture 4c/bw | DN | PN | Permissible pressure ps | Closing pressure Δps | Differential pressure ∆pmin value | Differential pressure Δpmax value | kvs | kvs (Sequence I) | kvs (Sequence II) | kvmax | kv variable | ﻿kvs theor. | kv (factory setting) | Vnom [l/s] | Vnom [l/min] | Vnom [l/h] | Vmaxpos1 | Vmaxpos2 | Vmaxpos3 | Vmax low-n | Control path leakage rate | Number of pipe connections | Pipe connection type | Measurement ports | Media | Valve application | Electrical accessories | Mechanical accessories | V0 | V1 | Version Number | Path
PdmarticleID | Label | 891 | 6667 | 6691 | 22 | 281 | 121 | 6517 | 6577 | 230 | 6650 | 118 | 112 | 83 | 260 | 144 | 406 | 660 | 3432 | 377 | 15 | 528 | 23 | 18 | 7308 | 28 | 14 | 510 | 511 | 78 | 6853 | 6827 | 6684 | 3460 | 6516 | 7153 | 548 | 549 | 7311 | 7456 | 6686 | 6560 | 6561 | 7312 | 6673 | 6666 | 581 | 582 | 7392 | 7393 | VersionNr | Path
61654 | R3032-16-S3 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2332 |  |  | 328 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 32\
61655 | R3040-16-S3 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2340 |  |  | 326 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 40\
101235 | EVC24A-SR | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 35 s / 40 mm | 2500 N |  | AC/DC 24 V |  | IP54 | EVC24A-SR | EVC24A-SR_datasheet_en-gb.pdf |  | PIC_EU_EVC24A-SR_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 259 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\EVC..A (2500N)\modulating\AC/DC 24 V\
101236 | RV24A-SZ | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 120 s / 40 mm | 4500 N |  | AC/DC 24 V |  | IP54 | RV24A-SZ | RV24A-SZ_datasheet_en-gb.pdf |  | PIC_EU_RV24A-SZ_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 261 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\RV..A (4500N)\modulating\AC/DC 24 V\
5294 | R3015-1-P4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 0.4 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 349 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5295 | R3015-1-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 0.63 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 350 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
4765 | NR24A | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NR24A | NR24A_datasheet_en-gb.pdf |  | PIC_EU_NR24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 323 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\Open-Close, 3-point\AC/DC 24 V\
4766 | NR24A-MF | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 |  | NR24A-MF_datasheet_en-gb.pdf |  | PIC_EU_NR24A-MF-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN |  |  |  | 300 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\modulating, MF\AC/DC 24 V\
5137 | H620R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 20 | 6 | 600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 283 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 20\
5138 | H625R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 25 | 6 | 600 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 286 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 25\
305193 | R3020-P63-4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 |  |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 21 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
4771 | NRC24A-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 45 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRC24A-SR | NRC24A-SR_datasheet_en-gb.pdf |  | PIC_EU_NR24A-MF-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 277 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\NRC..A (10 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4768 | NR24A-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NR24A-SR | NR24A-SR_datasheet_en-gb.pdf |  | PIC_EU_NR24A-SR-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 315 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5139 | H632R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 32 | 6 | 600 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 282 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 32\
61658 | R3050-25-S4 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2350 |  |  | 325 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 50\
101246 | LVC24A-MP-TPC | Globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  |  | 35 s / 15 mm | 500 N |  | AC/DC 24 V |  | IP54 | LVC24A-MP-TPC | LVC24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_LVC24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 332 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\LVC..A (500N)\modulating, MP\AC/DC 24 V\
101245 | LV24A-MP-TPC | Globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  |  | 150 s / 15 mm | 500 N |  | AC/DC 24 V |  | IP54 | LV24A-MP-TPC | LV24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_LV24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 332 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\LV..A (500N)\modulating, MP\AC/DC 24 V\
5298 | R3015-1P3-P25-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.3 m³/h | 0.25 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 346 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
61656 | R3040-25-S4 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2340 |  |  | 328 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 40\
101244 | EVC24A-MF | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 35 s / 40 mm | 2500 N |  | AC/DC 24 V |  | IP54 | EVC24A-MF | EVC24A-MF_datasheet_en-gb.pdf |  | PIC_EU_EVC24A-MF_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN |  |  |  | 295 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\EVC..A (2500N)\modulating, MF\AC/DC 24 V\
5300 | R3015-1P3-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.3 m³/h | 0.63 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 347 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
101237 | RV24A-SR | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 120 s / 40 mm | 4500 N |  | AC/DC 24 V |  | IP54 | RV24A-SR | RV24A-SR_datasheet_en-gb.pdf |  | PIC_EU_RV24A-SR_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 265 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\RV..A (4500N)\modulating\AC/DC 24 V\
5141 | H650R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 50 | 6 | 600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 287 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 50\
101247 | NV24A-MP-TPC | Globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NV24A-MP-TPC | NV24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_NV24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 335 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\NV..A (1000N)\modulating, MP\AC/DC 24 V\
5299 | R3015-1P3-P4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.3 m³/h | 0.4 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 346 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5301 | R3015-1P3-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.3 m³/h | 1 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 346 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5297 | R3015-1-1P3-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.3 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 346 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5142 | H664R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 65 | 6 | 600 kPa |  |  |  | 58 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 282 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 65\
5143 | H679R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 80 | 6 | 600 kPa |  |  |  | 90 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 283 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 80\
61659 | R3050-40-S4 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 40 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2350 |  |  | 329 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 50\
61662 | R3020-S2 | Change-over ball valve | CV | Valve | -10...120°C | [11 empty] | R3..-S.. | R3..-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2320 |  |  | 322 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, T-bore\DN 20\
5296 | R3015-1-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 349 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
4769 | NR230A | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC 230 V | 10 Nm | IP54 | NR230A | NR230A_datasheet_en-gb.pdf |  | PIC_EU_NRneutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 311 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\Open-Close, 3-point\AC 230 V\
61661 | R3015-S1 | Change-over ball valve | CV | Valve | -10...120°C | [11 empty] | R3..-S.. | R3..-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 15 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2315 |  |  | 328 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, T-bore\DN 15\
61660 | R3050-58-S4 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 58 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2350 |  |  | 327 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 50\
5144 | H6100R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 100 | 6 | 600 kPa |  |  |  | 145 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 280 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 100\
4767 | NR24A-S | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  | 1 x SPDT | AC/DC 24 V | 10 Nm | IP54 | NR24A-S | NR24A-S_datasheet_en-gb.pdf |  | PIC_EU_NR24A-S_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 316 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\Open-Close, 3-point\AC/DC 24 V\
5140 | H640R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 40 | 6 | 600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 284 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 40\
4770 | NR230A-S | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  | 1 x SPDT | AC 230 V | 10 Nm | IP54 | NR230A-S | NR230A-S_datasheet_en-gb.pdf |  | PIC_EU_NRneutral-S_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 320 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\Open-Close, 3-point\AC 230 V\
4773 | NRQ24A-SZ | Very fast running rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  | 9 s |  |  |  | AC/DC 24 V | 8 Nm | IP54 | NRQ24A-SZ | NRQ24A-SZ_datasheet_en-gb.pdf |  | PIC_EU_NRQ24A-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 288 | EU\Products\Water solutions\Rotary product range actuators\Very fast runner actuator\NRQ..A (8 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4774 | TR24 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 100 s |  |  |  | AC/DC 24 V | 2 Nm | IP40 | TR24 | TR24_datasheet_en-gb.pdf |  | PIC_EU_TR24_01_4C.jpg | [30 empty] | 300 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\TR.. (2 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
101248 | NVC24A-MP-TPC | Globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  |  | 35 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVC24A-MP-TPC | NVC24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVC24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 328 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\NVC..A (1000N)\modulating, MP\AC/DC 24 V\
101251 | EV24A-MP-TPC | Globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  |  | 150 s / 40 mm | 2500 N |  | AC/DC 24 V |  | IP54 | EV24A-MP-TPC | EV24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_EV24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 337 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\EV..A (2500N)\modulating, MP\AC/DC 24 V\
5148 | H613S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 279 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 15\
5149 | H614S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 277 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 15\
5150 | H615S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 277 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 15\
5145 | H610S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 0.4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 283 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 15\
4772 | NRQ24A-SR | Very fast running rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 9 s |  |  |  | AC/DC 24 V | 8 Nm | IP54 | NRQ24A-SR | NRQ24A-SR_datasheet_en-gb.pdf |  | PIC_EU_NRQ24A-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 283 | EU\Products\Water solutions\Rotary product range actuators\Very fast runner actuator\NRQ..A (8 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4776 | TR24-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 2 Nm | IP40 | TR24-SR | TR24-SR_datasheet_en-gb.pdf |  | PIC_EU_TR24_01_4C.jpg | [30 empty] | 319 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\TR.. (2 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
61669 | R3050-S4 | Change-over ball valve | CV | Valve | -10...120°C | [11 empty] | R3..-S.. | R3..-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 49 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2350 |  |  | 318 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, T-bore\DN 50\
61670 | R3015-BL1 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 5.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2315 |  |  | 324 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 15\
5303 | D625N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 25 | 6 / 10 / 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 45 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 307 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
61663 | R3025-S2 | Change-over ball valve | CV | Valve | -10...120°C | [11 empty] | R3..-S.. | R3..-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 26 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2325 |  |  | 314 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, T-bore\DN 25\
5304 | D632N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 32 | 6 / 10 / 16 | 1600 kPa |  |  | 5 kPa |  |  |  | 55 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 294 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
5307 | D665N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 65 | 6 / 10 / 16 | 1600 kPa |  |  | 7 kPa |  |  |  | 180 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
5146 | H611S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 275 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 15\
101249 | SV24A-MP-TPC | Globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  |  | 150 s / 20 mm | 1500 N |  | AC/DC 24 V |  | IP54 | SV24A-MP-TPC | SV24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_SV24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 338 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\SV..A (1500N)\modulating, MP\AC/DC 24 V\
5305 | D640N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 40 | 6 / 10 / 16 | 1600 kPa |  |  | 7 kPa |  |  |  | 70 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 296 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
101255 | NV24ALON | Globe valve actuator |  | Actuator |  | communicative |  | LON (FTT-10A) |  |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NV24ALON | NV24ALON_datasheet_en-gb.pdf |  | PIC_EU_NV24ALON_01_4c.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 325 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\NV..A (1000N)\modulating, LON\AC/DC 24 V\
5147 | H612S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 278 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 15\
101257 | NVK24A-SZ-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC / NO |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVK24A-SZ-TPC | NVK24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVK24A-SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 303 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVK..A (1000N)\modulating\AC/DC 24 V\
61671 | R3020-BL2 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 11 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2320 |  |  | 307 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 20\
61664 | R3032-S3 | Change-over ball valve | CV | Valve | -10...120°C | [11 empty] | R3..-S.. | R3..-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2332 |  |  | 314 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, T-bore\DN 32\
5302 | R3015-1P3-1P3-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.3 m³/h | 1.3 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 348 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
4782 | TRF24-2 | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NC | 90 s |  |  |  | AC 24 V | 2.5 Nm | IP42 | TRF24-2 | TRF24-2_datasheet_en-gb.pdf |  | PIC_EU_TRF-neutral_02_4C.jpg | [30 empty] | 340 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\3-point\AC/DC 24 V\
61667 | R3040-S3 | Change-over ball valve | CV | Valve | -10...120°C | [11 empty] | R3..-S.. | R3..-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 31 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2340 |  |  | 315 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, T-bore\DN 40\
5306 | D650N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 50 | 6 / 10 / 16 | 1600 kPa |  |  | 10 kPa |  |  |  | 90 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 296 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
101250 | SVC24A-MP-TPC | Globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  |  | 35 s / 20 mm | 1500 N |  | AC/DC 24 V |  | IP54 | SVC24A-MP-TPC | SVC24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_SVC24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 324 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\SVC..A (1500N)\modulating, MP\AC/DC 24 V\
4777 | TR230-3 | Rotary actuator |  | Actuator |  | 3-point |  |  |  | 105 s |  |  |  | AC 230 V | 2 Nm | IP40 | TR230-3 | TR230-3_datasheet_en-gb.pdf |  | PIC_EU_TR24_01_4C.jpg | [30 empty] | 289 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\TR.. (2 Nm)\Ball valve linkage\3-point\AC 230 V\
101258 | NVKC24A-SZ-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC / NO |  | 35 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVKC24A-SZ-TPC | NVKC24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVKC24A-SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 297 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVKC..A (1000N)\modulating\AC/DC 24 V\
4783 | TRF24-2-O | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NO | 90 s |  |  |  | AC 24 V | 2.5 Nm | IP42 | TRF24-2-O | TRF24-2-O_datasheet_en-gb.pdf |  | PIC_EU_TRF-O-neutral_01_4C.jpg | [30 empty] | 336 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\3-point\AC/DC 24 V\
4787 | TRF24-S-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 1 x SPDT | AC/DC 24 V | 2.5 Nm | IP42 | TRF24-S-O | TRF24-S-O_datasheet_en-gb.pdf |  | PIC_EU_TRF24-S_01_4C.jpg | [30 empty] | 368 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
101282 | NVK24A-MP-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus | NC / NO |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVK24A-MP-TPC | NVK24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVK24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 367 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVK..A (1000N)\modulating, MP\AC/DC 24 V\
101283 | NVKC24A-MP-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus | NC / NO |  | 35 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVKC24A-MP-TPC | NVKC24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVKC24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZN230-24MP¦ZFP2-MP |  |  |  | 353 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVKC..A (1000N)\modulating, MP\AC/DC 24 V\
5153 | H624S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 25 | 16 | 1600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 276 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 25\
61679 | R6015R1-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 303 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 15\
5309 | D6100N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 100 | 6 / 10 / 16 | 1600 kPa |  |  | 4 kPa |  |  |  | 580 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 301 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
101278 | NVK24A-SR-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC / NO |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVK24A-SR-TPC | NVK24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVK24A-SR-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 303 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVK..A (1000N)\modulating\AC/DC 24 V\
5151 | H619S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 20 | 16 | 1600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 277 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 20\
101284 | NVK24ALON | SuperCap globe valve actuator |  | Actuator |  | communicative |  | LON (FTT-10A) | NC / NO |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVK24ALON | NVK24ALON_datasheet_en-gb.pdf |  | PIC_EU_NVK24ALON_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 350 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVK..A (1000N)\modulating, LON\AC/DC 24 V\
4784 | TRF24 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC/DC 24 V | 2.5 Nm | IP42 | TRF24 | TRF24_datasheet_en-gb.pdf |  | PIC_EU_TRF24_01_4C.jpg | [30 empty] | 329 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5154 | H625S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 25 | 16 | 1600 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 275 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 25\
5155 | H632S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 32 | 16 | 1600 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 276 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 32\
5324 | R515 | Change-over ball valve | CV | Valve | 6...100°C | [11 empty] | R5.. | R5.._datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 8.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Change-over valve | ZR24-2 | ZR4515 |  |  | 307 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\External thread, 3-way, T-bore\DN 15\
61676 | R3040-BL3 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 14 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2340 |  |  | 300 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 40\
4788 | TRF24-SR | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 90 s |  |  |  | AC/DC 24 V | 2.5 Nm | IP42 | TRF24-SR | TRF24-SR_datasheet_en-gb.pdf |  | PIC_EU_TRF24-SR_01_4C.jpg | [30 empty] | 365 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5152 | H620S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 20 | 16 | 1600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 273 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 20\
101279 | NVKC24A-SR-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC / NO |  | 35 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVKC24A-SR-TPC | NVKC24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVKC24A-SR-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 300 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVKC..A (1000N)\modulating\AC/DC 24 V\
5156 | H640S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 40 | 16 | 1600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 40\
5308 | D680N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 80 | 6 / 10 / 16 | 1600 kPa |  |  | 6 kPa |  |  |  | 300 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 291 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
61677 | R3050-BL3 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 24 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2350 |  |  | 299 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 50\
61678 | R6015RP63-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 303 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 15\
5310 | D6125N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 125 | 6 / 10 / 16 | 1600 kPa |  |  | 4 kPa |  |  |  | 820 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150¦ZD6N-H150 |  |  | 289 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
61675 | R3032-BL3 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 32 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 15 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2332 |  |  | 302 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 32\
61672 | R3025-BL2 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2325 |  |  | 306 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 25\
4785 | TRF24-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC/DC 24 V | 2.5 Nm | IP42 | TRF24-O | TRF24-O_datasheet_en-gb.pdf |  | PIC_EU_TRF-O-neutral_01_4C.jpg | [30 empty] | 319 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5315 | D6350N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 350 | 10 / 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 10900 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S350 |  |  | 290 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
5311 | D6150N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 150 | 6 / 10 / 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 1600 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150¦ZD6N-H150 |  |  | 291 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
4786 | TRF24-S | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 1 x SPDT | AC/DC 24 V | 2.5 Nm | IP42 | TRF24-S | TRF24-S_datasheet_en-gb.pdf |  | PIC_EU_TRF24-S_01_4C.jpg | [30 empty] | 365 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
4790 | TRF230 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 230 V | 2.5 Nm | IP42 | TRF230 | TRF230_datasheet_en-gb.pdf |  | PIC_EU_TRF-neutral_02_4C.jpg | [30 empty] | 356 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC 230 V\
4791 | TRF230-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 230 V | 2.5 Nm | IP42 | TRF230-O | TRF230-O_datasheet_en-gb.pdf |  | PIC_EU_TRF-O-neutral_01_4C.jpg | [30 empty] | 349 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC 230 V\
101286 | AVK24A-SZ-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC / NO |  | 150 s / 32 mm | 2000 N |  | AC/DC 24 V |  | IP54 | AVK24A-SZ-TPC | AVK24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_AVK24A-SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 313 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\AVK..A (2000N)\modulating\AC/DC 24 V\
4793 | TRF230-S-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 1 x SPDT | AC 230 V | 2.5 Nm | IP42 | TRF230-S-O | TRF230-S-O_datasheet_en-gb.pdf |  | PIC_EU_TRF230-S-neutral_01_4C.jpg | [30 empty] | 373 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC 230 V\
101287 | AVK24A-SR-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC / NO |  | 150 s / 32 mm | 2000 N |  | AC/DC 24 V |  | IP54 | AVK24A-SR-TPC | AVK24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_AVK24A-SR-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 323 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\AVK..A (2000N)\modulating\AC/DC 24 V\
5357 | R404DK | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 10 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 0.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4510 |  |  | 305 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
61683 | R6020R6P3-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 20 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 304 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 20\
101541 | D625NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 25 | 10 / 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 45 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 202 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
101289 | AVK24ALON | SuperCap globe valve actuator |  | Actuator |  | communicative |  | LON (FTT-10A) | NC / NO |  | 150 s / 32 mm | 2000 N |  | AC/DC 24 V |  | IP54 | AVK24ALON | AVK24ALON_datasheet_en-gb.pdf |  | PIC_EU_AVK24ALON_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 352 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\AVK..A (2000N)\modulating, LON\AC/DC 24 V\
4806 | TRY24 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 35 s |  |  |  | AC/DC 24 V | 2 Nm | IP40 | TRY24 | TRY24_datasheet_en-gb.pdf |  | PIC_EU_TR24_01_4C.jpg | [30 empty] | 281 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\TR.. (2 Nm)\Ball valve linkage\3-point\AC/DC 24 V\
5157 | H650S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 50 | 16 | 1600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 275 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 50\
5159 | H665S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 65 | 16 | 1600 kPa |  |  |  | 63 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 267 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 65\
5329 | R540 | Change-over ball valve | CV | Valve | 6...100°C | [11 empty] | R5.. | R5.._datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Change-over valve | ZR24-2 | ZR4540 |  |  | 301 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\External thread, 3-way, T-bore\DN 40\
5158 | H664S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 65 | 16 | 1600 kPa |  |  |  | 58 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 65\
101542 | D632NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 32 | 10 / 16 | 1600 kPa |  |  | 5 kPa |  |  |  | 55 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 204 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5161 | H6100S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 100 | 16 | 1600 kPa |  |  |  | 145 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 268 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 100\
5160 | H680S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 80 | 16 | 1600 kPa |  |  |  | 100 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 80\
101288 | AVK24A-MP-TPC | SuperCap globe valve actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus | NC / NO |  | 150 s / 32 mm | 2000 N |  | AC/DC 24 V |  | IP54 | AVK24A-MP-TPC | AVK24A-MP-TPC_datasheet_en-gb.pdf |  | PIC_EU_AVK24A-MP-TPC_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 375 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\AVK..A (2000N)\modulating, MP\AC/DC 24 V\
61680 | R6015R1P6-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 296 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 15\
4792 | TRF230-S | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 1 x SPDT | AC 230 V | 2.5 Nm | IP42 | TRF230-S | TRF230-S_datasheet_en-gb.pdf |  | PIC_EU_TRF230-S-neutral_01_4C.jpg | [30 empty] | 376 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\Open-Close\AC 230 V\
61685 | R6032R16-B3 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 32 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 294 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 32\
61681 | R6015R2P5-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 298 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 15\
101543 | D640NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 40 | 10 / 16 | 1600 kPa |  |  | 7 kPa |  |  |  | 70 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 205 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
61684 | R6025R10-B2 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 25 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 298 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 25\
5325 | R520 | Change-over ball valve | CV | Valve | 6...100°C | [11 empty] | R5.. | R5.._datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 21 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Change-over valve | ZR24-2 | ZR4520 |  |  | 311 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\External thread, 3-way, T-bore\DN 20\
61682 | R6015R4-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 299 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 15\
5162 | H6125S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 125 | 16 | 1600 kPa |  |  |  | 220 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 272 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 125\
5330 | R550 | Change-over ball valve | CV | Valve | 6...100°C | [11 empty] | R5.. | R5.._datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 49 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Change-over valve | ZR24-2 | ZR4550 |  |  | 303 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\External thread, 3-way, T-bore\DN 50\
5326 | R525 | Change-over ball valve | CV | Valve | 6...100°C | [11 empty] | R5.. | R5.._datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 26 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Change-over valve | ZR24-2 | ZR4525 |  |  | 297 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\External thread, 3-way, T-bore\DN 25\
4789 | TRF24-SR-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NO | 90 s |  |  |  | AC/DC 24 V | 2.5 Nm | IP42 | TRF24-SR-O | TRF24-SR-O_datasheet_en-gb.pdf |  | PIC_EU_TRF24-SR-O_01_4C.jpg | [30 empty] | 333 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
61686 | R6040R25-B3 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 40 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 297 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 40\
5328 | R532 | Change-over ball valve | CV | Valve | 6...100°C | [11 empty] | R5.. | R5.._datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Change-over valve | ZR24-2 | ZR4532 |  |  | 301 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\External thread, 3-way, T-bore\DN 32\
101656 | NRF24A-SR | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SR | NRF24A-SR_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 220 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4808 | TRY230 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 35 s |  |  |  | AC 230 V | 2 Nm | IP40 | TRY230 | TRY230_datasheet_en-gb.pdf |  | PIC_EU_TR24_01_4C.jpg | [30 empty] | 295 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\TR.. (2 Nm)\Ball valve linkage\3-point\AC 230 V\
101659 | NRF24A-SR-S2-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NO | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SR-S2-O | NRF24A-SR-S2-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 233 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4824 | KR230 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 75 s |  |  |  | AC 230 V | 2 Nm | IP54 | KR230 | KR230_datasheet_en-gb.pdf |  | PIC_EU_KR24_01_4C.jpg | [27 empty] | Z-MA |  |  | 307 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\KR.. (2 Nm)\Ball valve linkage\3-point\AC 230 V\
5169 | H6125SP | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..SP | H6..SP_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 125 | 16 | 1600 kPa |  |  |  | 220 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 274 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\SP\DN 125\
61689 | R6020R-B1 | Open-close ball valve | CV | Valve | -10...100°C | [11 empty] | R6..R-B.. | R6..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 20 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  |  |  |  | 276 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Flange, 2-way, PN 6\DN 20\
5163 | H6150S | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..S | H6..S_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 150 | 16 | 1600 kPa |  |  |  | 320 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 270 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\S\DN 150\
5166 | H664SP | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..SP | H6..SP_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 65 | 16 | 1600 kPa |  |  |  | 58 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 276 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\SP\DN 65\
101660 | SRF24A-SR | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR | SRF24A-SR_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 226 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5164 | H640SP | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..SP | H6..SP_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 40 | 16 | 1600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 280 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\SP\DN 40\
5165 | H650SP | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..SP | H6..SP_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 50 | 16 | 1600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 277 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\SP\DN 50\
5362 | R409DK | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 10 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4510 |  |  | 292 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
4822 | KR24 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 75 s |  |  |  | AC/DC 24 V | 2 Nm | IP54 | KR24 | KR24_datasheet_en-gb.pdf |  | PIC_EU_KR24_01_4C.jpg | [27 empty] | Z-MA |  |  | 293 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\KR.. (2 Nm)\Ball valve linkage\3-point\AC/DC 24 V\
4925 | LR24A | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | LR24A | LR24A_datasheet_en-gb.pdf |  | PIC_EU_LR24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 357 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\Open-Close, 3-point\AC/DC 24 V\
5167 | H679SP | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..SP | H6..SP_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 80 | 16 | 1600 kPa |  |  |  | 90 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 275 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\SP\DN 80\
5358 | R405DK | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 10 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 0.4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4510 |  |  | 291 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
101657 | NRF24A-SR-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NO | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SR-O | NRF24A-SR-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 225 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
101658 | NRF24A-SR-S2 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SR-S2 | NRF24A-SR-S2_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 234 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
61687 | R6050R40-B3 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R6..Rxx-B.. | R6..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 50 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 40 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve |  |  |  |  | 300 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 2-way, PN 6\DN 50\
4823 | KR24-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 75 s |  |  |  | AC/DC 24 V | 2 Nm | IP54 | KR24-SR | KR24-SR_datasheet_en-gb.pdf |  | PIC_EU_KR24-SR_01_4C.jpg | [27 empty] | Z-MA |  |  | 304 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\KR.. (2 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5363 | R412D | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 15 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4515 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
5364 | R413D | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 15 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4515 |  |  | 292 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
61690 | R6025R-B2 | Open-close ball valve | CV | Valve | -10...100°C | [11 empty] | R6..R-B.. | R6..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 25 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 26 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  |  |  |  | 274 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Flange, 2-way, PN 6\DN 25\
4807 | TRY24-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 35 s |  |  |  | AC/DC 24 V | 2 Nm | IP40 | TRY24-SR | TRY24-SR_datasheet_en-gb.pdf |  | PIC_EU_TR24_01_4C.jpg | [30 empty] | 333 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\TR.. (2 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5360 | R407DK | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 10 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4510 |  |  | 292 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
101661 | SRF24A-SR-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NO | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR-O | SRF24A-SR-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 227 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5361 | R408DK | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 10 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4510 |  |  | 290 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
5359 | R406DK | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 10 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4510 |  |  | 293 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
61691 | R6032R-B3 | Open-close ball valve | CV | Valve | -10...100°C | [11 empty] | R6..R-B.. | R6..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 32 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  |  |  |  | 272 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Flange, 2-way, PN 6\DN 32\
5168 | H6100SP | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..SP | H6..SP_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 100 | 16 | 1600 kPa |  |  |  | 145 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 276 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\SP\DN 100\
61688 | R6015R-B1 | Open-close ball valve | CV | Valve | -10...100°C | [11 empty] | R6..R-B.. | R6..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 15 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  |  |  |  | 271 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Flange, 2-way, PN 6\DN 15\
4929 | LR230A | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC 230 V | 5 Nm | IP54 | LR230A | LR230A_datasheet_en-gb.pdf |  | PIC_EU_LR230A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 312 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\Open-Close, 3-point\AC 230 V\
101663 | SRF24A-SR-S2-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NO | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR-S2-O | SRF24A-SR-S2-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 246 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5385 | R415 | Open-close ball valve | CV | Valve | 6...100°C | [11 empty] | R4.. | R4.._datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 8.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve | ZR24-2 | ZR4515 |  |  | 312 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 15\
5365 | R414D | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 15 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4515 |  |  | 296 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
5175 | H715N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH715 |  |  | 268 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 15\
5173 | H713N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH715 |  |  | 268 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 15\
5367 | R418D | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 20 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4520 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 20\
61692 | R6040R-B3 | Open-close ball valve | CV | Valve | -10...100°C | [11 empty] | R6..R-B.. | R6..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 40 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 31 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  |  |  |  | 276 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Flange, 2-way, PN 6\DN 40\
101665 | SRF24A-SR-5-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NO | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR-5-O | SRF24A-SR-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 235 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
101662 | SRF24A-SR-S2 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR-S2 | SRF24A-SR-S2_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 242 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5366 | R417D | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 20 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4520 |  |  | 297 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 20\
101664 | SRF24A-SR-5 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR-5 | SRF24A-SR-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 241 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
5386 | R420 | Open-close ball valve | CV | Valve | 6...100°C | [11 empty] | R4.. | R4.._datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 21 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve | ZR24-2 | ZR4520 |  |  | 311 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 20\
61697 | R7020R6P3-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 20 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 301 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 20\
61307 | ZD6N-H100 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-H100 |  |  | PIC_EU_ZD6N-H_Manual control_BW.jpg | [30 empty] | 174 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
5170 | H6150SP | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..SP | H6..SP_datasheet_en-gb.pdf |  | PIC_EU_H6..S-neutral_01_4C.jpg | 150 | 16 | 1600 kPa |  |  |  | 320 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 274 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\SP\DN 150\
4927 | LR24A-S | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  | 1 x SPDT | AC/DC 24 V | 5 Nm | IP54 | LR24A-S | LR24A-S_datasheet_en-gb.pdf |  | PIC_EU_LR24A-S_02_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 319 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\Open-Close, 3-point\AC/DC 24 V\
5368 | R419D | Characterised control valve | CCV | Valve | 2...130°C | [11 empty] | R4xxD(K) | R4xxD(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 20 | 16 | 2700 kPa | 1400 kPa |  | 400 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve |  | ZR4520 |  |  | 292 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 20\
101666 | SRF24A-SR-S2-5 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR-S2-5 | SRF24A-SR-S2-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 249 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
101667 | SRF24A-SR-S2-5-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NO | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SR-S2-5-O | SRF24A-SR-S2-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 254 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
61693 | R6050R-B3 | Open-close ball valve | CV | Valve | -10...100°C | [11 empty] | R6..R-B.. | R6..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R6-neueCCV_01_SW.jpg | 50 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 49 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  |  |  |  | 273 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Flange, 2-way, PN 6\DN 50\
61695 | R7015R1P6-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 300 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 15\
5174 | H714N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH715 |  |  | 271 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 15\
4926 | LR24A-MF | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | LR24A-MF | LR24A-MF_datasheet_en-gb.pdf |  | PIC_EU_LR24A-MF_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦CR24-A3¦CR24-B3¦CRK24-B1 |  |  |  | 306 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\modulating, MF\AC/DC 24 V\
61308 | ZD6N-H150 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-H150 |  |  | PIC_EU_ZD6N-H_Manual control_BW.jpg | [30 empty] | 170 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
61694 | R7015RP63-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 305 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 15\
4928 | LR24A-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | LR24A-SR | LR24A-SR_datasheet_en-gb.pdf |  | PIC_EU_LR24A_SR_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 303 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
61698 | R7025R10-B2 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 25 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 300 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 25\
61696 | R7015R4-B1 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 293 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 15\
5171 | H711N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH715 |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 15\
4930 | LR230A-S | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  | 1 x SPDT | AC 230 V | 5 Nm | IP54 | LR230A-S | LR230A-S_datasheet_en-gb.pdf |  | PIC_EU_LR230A-S_02_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 324 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\Open-Close, 3-point\AC 230 V\
4931 | LRC24A-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 35 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | LRC24A-SR | LRC24A-SR_datasheet_en-gb.pdf |  | PIC_EU_LR24A-MF_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 279 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\LRC..A (5 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5172 | H712N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH715 |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 15\
61309 | ZD6N-S200 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S200 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 200 | [29 empty] | 201 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
4934 | LRF24-S | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 4 Nm | IP54 | LRF24-S | LRF24-S_datasheet_en-gb.pdf |  | PIC_EU_LRF..-S2_4C.jpg | [30 empty] | 332 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
4932 | LRF24 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC/DC 24 V | 4 Nm | IP54 | LRF24 | LRF24_datasheet_en-gb.pdf |  | PIC_EU_LRF230_01_4C.jpg | [30 empty] | 339 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5393 | R415D | Open-close ball valve | CV | Valve | 2...130°C | [11 empty] | R4..D(K) | R4..D(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 15 | 16 | 2700 kPa | 1400 kPa |  | 800 kPa | 12 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve |  | ZR4515 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 15\
127112 | CQ24A-MPL | Rotary actuator (ZoneTight) | QCV | Actuator |  | communicative |  | MP-Bus |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A-MPL | CQ24A-MPL_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-MPL_4C.jpg | [26 empty] | ZK2-GEN¦ZFP2-MP¦ZN230-24MP | ZCQ-E¦ZCQ-W |  |  | 258 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
127107 | CQ24A | Rotary actuator (ZoneTight) | QCV | Actuator |  | Open-close¦3-point |  |  |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A | CQ24A_datasheet_en-gb.pdf |  | PIC_EU_CQ24A_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 256 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
5180 | H750N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 50 | 16 | 1600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH750 |  |  | 272 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 50\
102367 | LR24A-MOD | Rotary actuator |  | Actuator |  | communicative |  | Modbus RTU |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | LR24A-MOD | LR24A-MOD_datasheet_en-gb.pdf |  | PIC_EU_LR24A-MP_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 277 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\modulating, MOD\AC/DC 24 V\
5179 | H740N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 40 | 16 | 1600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH740 |  |  | 270 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 40\
127110 | CQ230A | Rotary actuator (ZoneTight) | QCV | Actuator |  | Open-close¦3-point |  |  |  | 75 s |  |  |  | AC 230 V | 1 Nm | IP40 | CQ230A | CQ230A_datasheet_en-gb.pdf |  | PIC_EU_CQ24A_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 240 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
61311 | ZD6N-S350 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S350 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 350 | [29 empty] | 193 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
5387 | R425 | Open-close ball valve | CV | Valve | 6...100°C | [11 empty] | R4.. | R4.._datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 26 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve | ZR24-2 | ZR4525 |  |  | 299 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 25\
61319 | SRF24A-SZ-S2 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ-S2 | SRF24A-SZ-S2_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 320 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
61310 | ZD6N-S250 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S250 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 250 | [29 empty] | 209 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
61320 | SRF24A-SZ-S2-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NO | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ-S2-O | SRF24A-SZ-S2-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 324 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5391 | R450 | Open-close ball valve | CV | Valve | 6...100°C | [11 empty] | R4.. | R4.._datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 49 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve | ZR24-2 | ZR4550 |  |  | 302 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 50\
61703 | R7020R-B1 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R7..R-B.. | R7..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 20 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Change-over valve |  |  |  |  | 289 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Flange, 3-way, PN 6 \DN 20\
61316 | SRF24A-SZ | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ | SRF24A-SZ_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 315 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5178 | H732N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 32 | 16 | 1600 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH732 |  |  | 267 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 32\
5176 | H720N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 20 | 16 | 1600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH720 |  |  | 268 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 20\
5181 | H764N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 65 | 16 | 1600 kPa |  |  |  | 58 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C | ZH765 |  |  | 271 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 65\
5182 | H765N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 65 | 16 | 1600 kPa |  |  |  | 63 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C | ZH765 |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 65\
5392 | R410DK | Open-close ball valve | CV | Valve | 2...130°C | [11 empty] | R4..D(K) | R4..D(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 10 | 16 | 2700 kPa | 1400 kPa |  | 800 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve |  | ZR4510 |  |  | 296 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 10\
61700 | R7040R16-B3 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 40 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 299 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 40\
61702 | R7015R-B1 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R7..R-B.. | R7..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 15 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 15 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Change-over valve |  |  |  |  | 289 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Flange, 3-way, PN 6 \DN 15\
4936 | LRF24-SR | Spring-return rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC | 150 s |  |  |  | AC/DC 24 V | 4 Nm | IP54 | LRF24-SR | LRF24-SR_datasheet_en-gb.pdf |  | PIC_EU_LRF230_01_4C.jpg | [30 empty] | 328 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5390 | R440 | Open-close ball valve | CV | Valve | 6...100°C | [11 empty] | R4.. | R4.._datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve | ZR24-2 | ZR4540 |  |  | 298 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 40\
61699 | R7032R16-B3 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 32 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 302 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 32\
4935 | LRF24-S-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 4 Nm | IP54 | LRF24-S-O | LRF24-S-O_datasheet_en-gb.pdf |  | PIC_EU_LRF..-S2_4C.jpg | [30 empty] | 330 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5389 | R432 | Open-close ball valve | CV | Valve | 6...100°C | [11 empty] | R4.. | R4.._datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 400 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve | ZR24-2 | ZR4532 |  |  | 304 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 32\
61705 | R7032R-B3 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R7..R-B.. | R7..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 32 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Change-over valve |  |  |  |  | 285 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Flange, 3-way, PN 6 \DN 32\
61704 | R7025R-B2 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R7..R-B.. | R7..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 25 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 26 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Change-over valve |  |  |  |  | 282 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Flange, 3-way, PN 6 \DN 25\
127111 | CQ24A-SZ | Rotary actuator (ZoneTight) | QCV | Actuator |  | modulating | DC 0.5...10 V |  |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A-SZ | CQ24A-SZ_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-SZ_4C.jpg | [26 empty] | CR24-A3¦CR24-B3 | ZCQ-E¦ZCQ-W |  |  | 228 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
5394 | R420D | Open-close ball valve | CV | Valve | 2...130°C | [11 empty] | R4..D(K) | R4..D(K)_datasheet_en-gb.pdf |  | PIC_EU_R415D_01_4C.jpg | 20 | 16 | 2700 kPa | 1400 kPa |  | 800 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Shutt-off valve |  | ZR4520 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\External thread, 2-way\DN 20\
61701 | R7050R25-B3 | Characterised control valve | CCV | Valve | -10...100°C | [11 empty] | R7..Rxx-B.. | R7..Rxx-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 50 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Control valve |  |  |  |  | 305 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Flange, 3-way\DN 50\
4937 | LRF230 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 230 V | 4 Nm | IP54 | LRF230 | LRF230_datasheet_en-gb.pdf |  | PIC_EU_LRF230_01_4C.jpg | [30 empty] | 340 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC 230 V\
5177 | H725N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 25 | 16 | 1600 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 | ZH725 |  |  | 271 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 25\
61317 | SRF24A-SZ-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NO | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ-O | SRF24A-SZ-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 315 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4933 | LRF24-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC/DC 24 V | 4 Nm | IP54 | LRF24-O | LRF24-O_datasheet_en-gb.pdf |  | PIC_EU_LRF230_01_4C.jpg | [30 empty] | 333 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
61826 | SRFA-5 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA-5 | SRFA-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 290 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 24...240V / DC 24...125V\
61356 | NRF230A-3-S2 | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NC | 90 s |  |  | 2 x SPDT | AC 230 V | 10 Nm | IP54 | NRF230A-3-S2 | NRF230A-3-S2_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 316 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
140733 | NR24A-MOD | Rotary actuator |  | Actuator |  | communicative |  | Modbus RTU |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NR24A-MOD | NR24A-MOD_datasheet_en-gb.pdf |  | PIC_EU_LR24A-MP_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 258 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\modulating, MOD\AC/DC 24 V\
4938 | LRF230-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 230 V | 4 Nm | IP54 | LRF230-O | LRF230-O_datasheet_en-gb.pdf |  | PIC_EU_LRF230_01_4C.jpg | [30 empty] | 335 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC 230 V\
5469 | H7025Y10-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 25 | 40 | 4000 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 264 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 25\
5184 | H780N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 80 | 16 | 1600 kPa |  |  |  | 100 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C | ZH780 |  |  | 267 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 80\
61706 | R7040R-B3 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R7..R-B.. | R7..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 40 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 31 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Change-over valve |  |  |  |  | 285 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Flange, 3-way, PN 6 \DN 40\
5186 | H7125N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 125 | 16 | 1600 kPa |  |  |  | 220 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-D | ZH7125 |  |  | 270 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 125\
127225 | SRC24A-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 35 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRC24A-SR | SRC24A-SR_datasheet_en-gb.pdf |  | PIC_EU_SRC24A-SR_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 227 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\SRC..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4942 | LRQ24A-SZ | Very fast running rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  | 9 s |  |  |  | AC/DC 24 V | 4 Nm | IP54 | LRQ24A-SZ | LRQ24A-SZ_datasheet_en-gb.pdf |  | PIC_EU_LRQ24A-neutral_02_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 317 | EU\Products\Water solutions\Rotary product range actuators\Very fast runner actuator\LRQ..A (4 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
61355 | NRF230A-3-O | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NO | 90 s |  |  |  | AC 230 V | 10 Nm | IP54 | NRF230A-3-O | NRF230A-3-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 315 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
61354 | NRF230A-3 | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NC | 90 s |  |  |  | AC 230 V | 10 Nm | IP54 | NRF230A-3 | NRF230A-3_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 313 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
61387 | R6065W63-S8 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R6..W..-S8 | R6..W..-S8_datasheet_en-gb.pdf |  | PIC_EU_R6-W-S8-neutral_BW.jpg | 65 | 16 | 1600 kPa | 690 kPa |  | 400 kPa | 63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve | ZR24-F05 |  |  |  | 322 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Regel-Kugelhahnen\Flansch, 2-Weg, PN 16\DN 65\
5465 | H7200W630-S7 | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..W..S7 | H7..W..S7_datasheet_en-gb.pdf |  | PIC_EU_H7..W..S7_01_SW.jpg | 200 | 16 | 1600 kPa |  |  |  | 630 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-D |  |  |  | 277 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\W\DN 200\
4943 | NRF24A-SZ | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SZ | NRF24A-SZ_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 313 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
145518 | NV24A-MOD | Globe valve actuator |  | Actuator |  | communicative |  | Modbus RTU |  |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NV24A-MOD | NV24A-MOD_datasheet_en-gb.pdf |  | PIC_EU_NV24ALON_01_4c.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 296 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\NV..A (1000N)\modulating, MOD\AC/DC 24 V\
4939 | LRF230-S | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC 230 V | 4 Nm | IP54 | LRF230-S | LRF230-S_datasheet_en-gb.pdf |  | PIC_EU_LRF..-S2_4C.jpg | [30 empty] | 340 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC 230 V\
5185 | H7100N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 100 | 16 | 1600 kPa |  |  |  | 145 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C | ZH7100 |  |  | 267 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 100\
5183 | H779N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 80 | 16 | 1600 kPa |  |  |  | 90 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C | ZH780 |  |  | 270 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 80\
5187 | H7150N | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..N | H7..N_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 150 | 16 | 1600 kPa |  |  |  | 320 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-D | ZH7150 |  |  | 265 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\N\DN 150\
5470 | H7032Y16-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 32 | 40 | 4000 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 259 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 32\
61707 | R7050R-B3 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R7..R-B.. | R7..R-B.._datasheet_en-gb.pdf |  | PIC_EU_R7-neueCCV_01_SW.jpg | 50 | 6 | 600 kPa | 600 kPa |  | 100 kPa | 49 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Flange |  | Water | Change-over valve |  |  |  |  | 284 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Flange, 3-way, PN 6 \DN 50\
5468 | H7020Y6P3-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 20 | 40 | 4000 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 263 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 20\
5188 | H711R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 268 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 15\
61734 | SRQ24A | Very fast running rotary actuator |  | Actuator |  | Open-close |  |  |  | 9 s |  |  |  | AC/DC 24 V | 16 Nm | IP54 | SRQ24A | SRQ24A_datasheet_en-gb.pdf |  | PIC_EU_GR230A-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 300 | EU\Products\Water solutions\Rotary product range actuators\Very fast runner actuator\SRQ..A (20 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
4944 | NRF24A-SZ-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NO | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SZ-O | NRF24A-SZ-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 314 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
61823 | R3050-BL4 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 75 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2350 |  |  | 293 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 50\
5466 | H7250W1000-S7 | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..W..S7 | H7..W..S7_datasheet_en-gb.pdf |  | PIC_EU_H7..W..S7_01_SW.jpg | 250 | 16 | 1600 kPa |  |  |  | 1000 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-D |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\3-way\W\DN 250\
61822 | R3040-BL4 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 47 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2340 |  |  | 296 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 40\
61357 | NRF230A-3-S2-O | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NO | 90 s |  |  | 2 x SPDT | AC 230 V | 10 Nm | IP54 | NRF230A-3-S2-O | NRF230A-3-S2-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 307 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
4940 | LRF230-S-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC 230 V | 4 Nm | IP54 | LRF230-S-O | LRF230-S-O_datasheet_en-gb.pdf |  | PIC_EU_LRF..-S2_4C.jpg | [30 empty] | 341 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\Open-Close\AC 230 V\
5467 | H7015Y4-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 15 | 40 | 4000 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 15\
4941 | LRQ24A-SR | Very fast running rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 9 s |  |  |  | AC/DC 24 V | 4 Nm | IP54 | LRQ24A-SR | LRQ24A-SR_datasheet_en-gb.pdf |  | PIC_EU_LRQ24A-neutral_02_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 328 | EU\Products\Water solutions\Rotary product range actuators\Very fast runner actuator\LRQ..A (4 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
253470 | CQ24A-SZ-T | Rotary actuator (ZoneTight) | QCV | Actuator |  | modulating | DC 0.5...10 V |  |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A-SZ-T | CQ24A-SZ-T_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-SZ-T_4C.jpg | [26 empty] | CR24-A3¦CR24-B3 | ZCQ-E¦ZCQ-W |  |  | 227 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
61832 | SRFA-S2 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA-S2 | SRFA-S2_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 281 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
4945 | NRF24A-SZ-S2 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SZ-S2 | NRF24A-SZ-S2_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 324 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
4949 | NRFD230A-3-S2 | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NC | 35 s |  |  | 2 x SPDT | AC 230 V | 5 Nm | IP54 | NRFD230A-3-S2 | NRFD230A-3-S2_datasheet_en-gb.pdf |  | PIC_EU_NRFD230A-3_S2_neutral_01_4C.jpg | [30 empty] | 316 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
61398 | SRF230A-S2-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC 230 V | 20 Nm | IP54 | SRF230A-S2-O | SRF230A-S2-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 299 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 230 V\
4946 | NRF24A-SZ-S2-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NO | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 10 Nm | IP54 | NRF24A-SZ-S2-O | NRF24A-SZ-S2-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 322 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5473 | H7065Y63-S4 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 65 | 40 | 4000 kPa |  |  |  | 63 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 264 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 65\
5189 | H712R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 265 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 15\
61399 | SRF230A-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 230 V | 20 Nm | IP54 | SRF230A-O | SRF230A-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 291 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 230 V\
4950 | NRFD230A-3-S2-O | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NO | 35 s |  |  | 2 x SPDT | AC 230 V | 5 Nm | IP54 | NRFD230A-3-S2-O | NRFD230A-3-S2-O_datasheet_en-gb.pdf |  | PIC_EU_NRFD230A-3_S2_neutral_01_4C.jpg | [30 empty] | 315 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
253471 | CQ24A-MPL-T | Rotary actuator (ZoneTight) | QCV | Actuator |  | communicative |  | MP-Bus |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A-MPL-T | CQ24A-MPL-T_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-MPL-T-ret_4C.jpg | [26 empty] | ZK2-GEN¦ZFP2-MP¦ZN230-24MP | ZCQ-E¦ZCQ-W |  |  | 243 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
61396 | R6150W320-S8 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R6..W..-S8 | R6..W..-S8_datasheet_en-gb.pdf |  | PIC_EU_R6-W-S8-neutral_BW.jpg | 150 | 16 | 1600 kPa | 690 kPa |  | 400 kPa | 320 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve | ZR24-F05 |  |  |  | 306 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Regel-Kugelhahnen\Flansch, 2-Weg, PN 16\DN 150\
5190 | H713R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 15\
4947 | NRFD230A-3 | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NC | 35 s |  |  |  | AC 230 V | 5 Nm | IP54 | NRFD230A-3 | NRFD230A-3_datasheet_en-gb.pdf |  | PIC_EU_NRFD230A-3_neutral_02_4C.jpg | [30 empty] | 320 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
5191 | H714R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 15\
5471 | H7040Y25-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 40 | 40 | 4000 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 264 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 40\
61400 | SRF24A-S2-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-S2-O | SRF24A-S2-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 310 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
253468 | CQ24A-T | Rotary actuator (ZoneTight) | QCV | Actuator |  | Open-close¦3-point |  |  |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A-T | CQ24A-T_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-T_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 227 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
61830 | SRFA | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA | SRFA_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 292 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
253469 | CQ230A-T | Rotary actuator (ZoneTight) | QCV | Actuator |  | Open-close¦3-point |  |  |  | 75 s |  |  |  | AC 230 V | 1 Nm | IP40 | CQ230A-T | CQ230A-T_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-T_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 233 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
5193 | H720R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 20 | 6 | 600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 271 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 20\
5476 | H7015X4-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 15 | 25 | 2500 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 259 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 15\
61827 | SRFA-5-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA-5-O | SRFA-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 279 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 24...240V / DC 24...125V\
5192 | H715R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 266 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 15\
5472 | H7050Y40-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 50 | 40 | 4000 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 263 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 50\
61829 | SRFA-S2-5-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA-S2-5-O | SRFA-S2-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 289 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 24...240V / DC 24...125V\
5474 | H7080Y100-S4 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 80 | 40 | 4000 kPa |  |  |  | 100 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 265 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 80\
5475 | H7100Y160-S4 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..Y..S.. | H7..Y..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 100 | 40 | 4000 kPa |  |  |  | 160 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 264 | EU\Products\Water solutions\Globe valve range valves\PN40, flange\3-way\Y\DN 100\
61389 | R6080W100-S8 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R6..W..-S8 | R6..W..-S8_datasheet_en-gb.pdf |  | PIC_EU_R6-W-S8-neutral_BW.jpg | 80 | 16 | 1600 kPa | 690 kPa |  | 400 kPa | 100 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve | ZR24-F05 |  |  |  | 308 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Regel-Kugelhahnen\Flansch, 2-Weg, PN 16\DN 80\
4948 | NRFD230A-3-O | Spring-return rotary actuator |  | Actuator |  | 3-point |  |  | NO | 35 s |  |  |  | AC 230 V | 5 Nm | IP54 | NRFD230A-3-O | NRFD230A-3-O_datasheet_en-gb.pdf |  | PIC_EU_NRFD230A-3_neutral_02_4C.jpg | [30 empty] | 318 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\3-point\AC 230 V\
61831 | SRFA-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA-O | SRFA-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 283 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
61393 | R6100W160-S8 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R6..W..-S8 | R6..W..-S8_datasheet_en-gb.pdf |  | PIC_EU_R6-W-S8-neutral_BW.jpg | 100 | 16 | 1600 kPa | 690 kPa |  | 400 kPa | 160 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve | ZR24-F05 |  |  |  | 315 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Regel-Kugelhahnen\Flansch, 2-Weg, PN 16\DN 100\
61395 | R6125W250-S8 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R6..W..-S8 | R6..W..-S8_datasheet_en-gb.pdf |  | PIC_EU_R6-W-S8-neutral_BW.jpg | 125 | 16 | 1600 kPa | 690 kPa |  | 400 kPa | 250 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Control valve | ZR24-F05 |  |  |  | 306 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Regel-Kugelhahnen\Flansch, 2-Weg, PN 16\DN 125\
61828 | SRFA-S2-5 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA-S2-5 | SRFA-S2-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 300 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 24...240V / DC 24...125V\
272362 | EP015R+MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | EP..R+MP | EP..R+MP_datasheet_en-gb.pdf |  | PIC_EU_EP040R+MP_4C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 2.9 m³/h |  | 0.35 l/s | 21 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 292 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
5194 | H725R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 25 | 6 | 600 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 267 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 25\
4957 | SR24A-SR-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24A-SR-5 | SR24A-SR-5_datasheet_en-gb.pdf |  | PIC_EU_SR24A-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 345 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
4951 | SR24A | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24A | SR24A_datasheet_en-gb.pdf |  | PIC_EU_SR24A_01_4c.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 348 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\Open-Close, 3-point\AC/DC 24 V\
4952 | SR24A-MF | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 |  | SR24A-MF_datasheet_en-gb.pdf |  | PIC_EU_SR24A-MF_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN |  |  |  | 349 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\modulating, MF\AC/DC 24 V\
5477 | H7020X6P3-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 20 | 25 | 2500 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 254 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 20\
5481 | H7050X40-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 50 | 25 | 2500 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 256 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 50\
69684 | R2050-25-S4 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2350 |  |  | 299 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 50\
61406 | SRF24A-SZ-5 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ-5 | SRF24A-SZ-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 302 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
61401 | SRF24A-5 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-5 | SRF24A-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 285 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
61402 | SRF24A-5-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-5-O | SRF24A-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 281 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
61833 | SRFA-S2-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC 24...240 V / DC 24...125 V | 20 Nm | IP54 | SRFA-S2-O | SRFA-S2-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 288 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
5199 | H779R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 80 | 6 | 600 kPa |  |  |  | 90 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 266 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 80\
5483 | H7080X100-S4 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 80 | 25 | 2500 kPa |  |  |  | 100 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 252 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 80\
5198 | H764R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 65 | 6 | 600 kPa |  |  |  | 58 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 267 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 65\
5478 | H7025X10-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 25 | 25 | 2500 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 258 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 25\
5479 | H7032X16-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 32 | 25 | 2500 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 257 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 32\
272612 | EP050R+MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | EP..R+MP | EP..R+MP_datasheet_en-gb.pdf |  | PIC_EU_EP040R+MP_4C.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 32.0 m³/h |  | 4.8 l/s | 288 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 259 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
272610 | EP032R+MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | EP..R+MP | EP..R+MP_datasheet_en-gb.pdf |  | PIC_EU_EP040R+MP_4C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 14.2 m³/h |  | 1.8 l/s | 108 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 264 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
69685 | R2050-40-S4 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 40 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2350 |  |  | 301 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 50\
69705 | R3032-BL2 | Change-over ball valve | CV | Valve | -10...100°C | [11 empty] | R3..-BL.. | R3..-BL.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 32 | 16 | 1600 kPa | 500 kPa |  | 350 kPa | 9 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Change-over valve |  | ZR2332 |  |  | 292 | EU\Products\Water solutions\Rotary product range valves\Change-over ball valve\Internal thread, 3-way, L-bore\DN 32\
63756 | RV24A-MF | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 120 s / 40 mm | 4500 N |  | AC/DC 24 V |  | IP54 | RV24A-MF | RV24A-MF_datasheet_en-gb.pdf |  | PIC_EU_RV24A-MF_01_4C.jpg | [26 empty] | S2A-H¦ZK1-GEN¦ZK2-GEN |  |  |  | 417 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\RV..A (4500N)\modulating, MF\AC/DC 24 V\
5197 | H750R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 50 | 6 | 600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 266 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 50\
5200 | H7100R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 100 | 6 | 600 kPa |  |  |  | 145 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 267 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 100\
61403 | SRF24A-S2-5 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-S2-5 | SRF24A-S2-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 301 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
61405 | SRF230A-S2-5 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC 230 V | 20 Nm | IP54 | SRF230A-S2-5 | SRF230A-S2-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 302 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 230 V\
272608 | EP020R+MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | EP..R+MP | EP..R+MP_datasheet_en-gb.pdf |  | PIC_EU_EP040R+MP_4C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 4.9 m³/h |  | 0.65 l/s | 39 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 266 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
5196 | H740R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 40 | 6 | 600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 269 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 40\
5221 | R405K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 310 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
69686 | R2050-S4 | Open-close ball valve | CV | Valve | -10...120°C | [11 empty] | R2..-S.. | R2..-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 49 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Shutt-off valve |  | ZR2350 |  |  | 289 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Internal thread, 2-way\DN 50\
4956 | SR24A-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24A-SR | SR24A-SR_datasheet_en-gb.pdf |  | PIC_EU_SR24A-SR_01_4c.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 324 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
69679 | R2020-8P6-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 8.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2320 |  |  | 310 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 20\
4953 | SR24A-MF-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24A-MF-5 | SR24A-MF-5_datasheet_en-gb.pdf |  | PIC_EU_SR24A-MF-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN |  |  |  | 352 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Butterfly valve linkage\modulating, MF\AC/DC 24 V\
5195 | H732R | Globe valve | H | Valve | 5...120°C | [11 empty] | H7..R | H7..R_datasheet_en-gb.pdf |  | PIC_EU_H7..N-neutral_01_4C.jpg | 32 | 6 | 600 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 266 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\3-way\reduced\DN 32\
272611 | EP040R+MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | EP..R+MP | EP..R+MP_datasheet_en-gb.pdf |  | PIC_EU_EP040R+MP_4C.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 21.3 m³/h |  | 2.5 l/s | 150 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 262 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
5480 | H7040X25-S2 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 40 | 25 | 2500 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 256 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 40\
4955 | SR24A-S | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  | 1 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SR24A-S | SR24A-S_datasheet_en-gb.pdf |  | PIC_EU_SR24A-S_01_4c.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 332 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\Open-Close, 3-point\AC/DC 24 V\
61404 | SRF230A-5 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 230 V | 20 Nm | IP54 | SRF230A-5 | SRF230A-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 306 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 230 V\
272609 | EP025R+MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | EP..R+MP | EP..R+MP_datasheet_en-gb.pdf |  | PIC_EU_EP040R+MP_4C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 8.6 m³/h |  | 1.15 l/s | 69 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 264 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
272617 | EV015R+BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | EV..R+BAC | EV..R+BAC_datasheet_en-gb.pdf |  | PIC_EU_EV032R+BAC_4C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 2.9 m³/h |  | 0.35 l/s | 21 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | Z-STRJ.1¦ZK1-GEN |  |  |  | 256 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
5482 | H7065X63-S4 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 65 | 25 | 2500 kPa |  |  |  | 63 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 254 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 65\
99762 | ZD6N-S450 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S450 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 450 | [29 empty] | 179 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
61412 | SRF24A-S2-5-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-S2-5-O | SRF24A-S2-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 294 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
61408 | SRF24A-SZ-S2-5 | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ-S2-5 | SRF24A-SZ-S2-5_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 313 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
61410 | SRF230A-S2-5-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC 230 V | 20 Nm | IP54 | SRF230A-S2-5-O | SRF230A-S2-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 303 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 230 V\
5486 | H6015XP63-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 15 | 25 | 2500 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 304 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 15\
5222 | R406K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 307 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
275742 | NV230A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 20 mm | 1000 N |  | AC 230 V |  | IP54 | NV230A-TPC | NV230A-TPC_datasheet_en-gb.pdf |  | PIC_EU_NV230A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 155 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\NV..A (1000N)\Open-Close, 3-point\AC 230 V\
5227 | R410 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 323 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
61409 | SRF24A-SZ-S2-5-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NO | 90 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ-S2-5-O | SRF24A-SZ-S2-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 316 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
5487 | H6015X1-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 15 | 25 | 2500 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 305 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 15\
5223 | R407K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 305 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
69775 | GRK24A-SR-5 | SuperCap rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  | NC / NO | 150 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GRK24A-SR-5 | GRK24A-SR-5_datasheet_en-gb.pdf |  | PIC_EU_GRKA_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 296 | EU\Products\Water solutions\Rotary product range actuators\SuperCap actuators\GRK..A\modulating\AC/DC 24 V\
99763 | ZD6N-S500 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S500 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 500 | [29 empty] | 180 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
99761 | ZD6N-S400 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S400 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 400 | [29 empty] | 176 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
99759 | ZD6N-S100 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S100 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 100 | [29 empty] | 178 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
272622 | EV050R+BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | EV..R+BAC | EV..R+BAC_datasheet_en-gb.pdf |  | PIC_EU_EV032R+BAC_4C.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 32.0 m³/h |  | 4.8 l/s | 288 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | Z-STRJ.1¦ZK1-GEN |  |  |  | 251 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
5489 | H6015X2P5-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 15 | 25 | 2500 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 303 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 15\
272618 | EV020R+BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | EV..R+BAC | EV..R+BAC_datasheet_en-gb.pdf |  | PIC_EU_EV032R+BAC_4C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 4.9 m³/h |  | 0.65 l/s | 39 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | Z-STRJ.1¦ZK1-GEN |  |  |  | 248 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
275830 | GRC24G-MF-T-5 | IP66/Nema4 actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 35 s |  |  |  | AC/DC 24 V | 40 Nm | IP66 | GRC24G-MF-T-5 | GRC24G-MF-T-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24G-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦HH24-MG¦HT24-MG¦ZK1-GEN¦ZK2-GEN |  |  |  | 196 | EU\Products\Water solutions\Rotary product range actuators\IP66/NEMA4 actuator\DRC..G\Butterfly valve linkage\modulating, MF\AC/DC 24 V\
5224 | R408K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 308 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
4967 | SR230P | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC 230 V | 20 Nm | IP66 + IP67 | SR230P | SR230P_datasheet_en-gb.pdf |  | PIC_EU_Robustline-Water_1cab_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 354 | EU\Products\Water solutions\Rotary product range actuators\RobustLine actuators\SR..P (20 Nm)\Ball valve linkage\Open-Close, 3-point\AC 230 V\
4960 | SR230A-S | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  | 1 x SPDT | AC 230 V | 20 Nm | IP54 | SR230A-S | SR230A-S_datasheet_en-gb.pdf |  | PIC_EU_SR230A-S_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 335 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\Open-Close, 3-point\AC 230 V\
5225 | R409K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 306 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 10\
4968 | SR24P | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP66 + IP67 | SR24P | SR24P_datasheet_en-gb.pdf |  | PIC_EU_Robustline-Water_1cab_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 325 | EU\Products\Water solutions\Rotary product range actuators\RobustLine actuators\SR..P (20 Nm)\Ball valve linkage\Open-Close, 3-point\AC/DC 24 V\
4958 | SR24P-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP66 + IP67 | SR24P-SR | SR24P-SR_datasheet_en-gb.pdf |  | PIC_EU_Robustline-Water_1cab_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 318 | EU\Products\Water solutions\Rotary product range actuators\RobustLine actuators\SR..P (20 Nm)\Ball valve linkage\modulating \AC/DC 24 V\
99760 | ZD6N-S150 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S150 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 150 | [29 empty] | 184 | EU\Produkte\Wasseranwendungen\Drehsortiment Antriebe\Manuelle Antriebe\
4993 | GV12-24-SR-T | Large stroke actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 82 s / 65 mm | 12000 N |  | AC/DC 24 V |  | IP65 | GV12-24-SR-T | GV12-24-SR-T_datasheet_en-gb.pdf |  | PIC_EU_GV12-neutral_01_4C.jpg | [30 empty] | 301 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\GV.. (12000N)\modulating\AC/DC 24 V\
61407 | SRF24A-SZ-5-O | Spring-return rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NO | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-SZ-5-O | SRF24A-SZ-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 298 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
5488 | H6015X1P6-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 15 | 25 | 2500 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 304 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 15\
272619 | EV025R+BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | EV..R+BAC | EV..R+BAC_datasheet_en-gb.pdf |  | PIC_EU_EV032R+BAC_4C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 8.6 m³/h |  | 1.15 l/s | 69 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | Z-STRJ.1¦ZK1-GEN |  |  |  | 247 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
61411 | SRF230A-5-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 230 V | 20 Nm | IP54 | SRF230A-5-O | SRF230A-5-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 299 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 230 V\
5484 | H7100X160-S4 | Globe valve | H | Valve | 5...200°C | [11 empty] | H7..X..S.. | H7..X..S.._datasheet_en-gb.pdf |  | PIC_EU_H7..X-S2-neutral_01_4C.jpg | 100 | 25 | 2500 kPa |  |  |  | 160 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | Flange |  | Water | Control valve |  |  |  |  | 253 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\3-way\X\DN 100\
4959 | SR230A | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC 230 V | 20 Nm | IP54 | SR230A | SR230A_datasheet_en-gb.pdf |  | PIC_EU_SR230A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 343 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\Open-Close, 3-point\AC 230 V\
272620 | EV032R+BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | EV..R+BAC | EV..R+BAC_datasheet_en-gb.pdf |  | PIC_EU_EV032R+BAC_4C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 14.2 m³/h |  | 1.8 l/s | 108 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | Z-STRJ.1¦ZK1-GEN |  |  |  | 256 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
5226 | R409 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 312 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
272621 | EV040R+BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | EV..R+BAC | EV..R+BAC_datasheet_en-gb.pdf |  | PIC_EU_EV032R+BAC_4C.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | [5 empty] | 21.3 m³/h |  | 2.5 l/s | 150 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent | Z-STRJ.1¦ZK1-GEN |  |  |  | 246 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
5485 | H6015XP4-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 15 | 25 | 2500 kPa |  |  |  | 0.4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 305 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 15\
4961 | SR230A-SR-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC 230 V | 20 Nm | IP54 | SR230A-SR-5 | SR230A-SR-5_datasheet_en-gb.pdf |  | PIC_EU_SR230A-SR-5_02_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 391 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Butterfly valve linkage\modulating\AC 230 V\
99789 | SRC24A-SR-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 35 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRC24A-SR-5 | SRC24A-SR-5_datasheet_en-gb.pdf |  | PIC_EU_SRC24A-SR-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 277 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\SRC..A (20 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
277660 | DRC24G-7 | IP66/Nema4 actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 90 Nm | IP66 | DRC24G-7 | DRC24G-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24G-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦HH24-MG¦HT24-MG |  |  |  | 110 | EU\Products\Water solutions\Rotary product range actuators\IP66/NEMA4 actuator\DRC..G\Butterfly valve linkage\Open-Close\AC/DC 24 V\
276521 | DR230A-7 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 150 s |  |  |  | AC 230 V | 90 Nm | IP54 | DR230A-7 | DR230A-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 142 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\Open-Close\AC 230 V\
5037 | NRF24A | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRF24A | NRF24A_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 333 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
4994 | GV12-230-3-T | Large stroke actuator |  | Actuator |  | 3-point |  |  |  |  | 82 s / 65 mm | 12000 N | 2 x SPDT | AC 230 V |  | IP65 | GV12-230-3-T | GV12-230-3-T_datasheet_en-gb.pdf |  | PIC_EU_GV12-neutral_01_4C.jpg | [30 empty] | 317 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\GV.. (12000N)\3-point\AC 230 V\
99970 | SR24P-SR-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP66 + IP67 | SR24P-SR-5 | SR24P-SR-5_datasheet_en-gb.pdf |  | PIC_EU_Robustline-Water_1cab_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 256 | EU\Products\Water solutions\Rotary product range actuators\RobustLine actuators\SR..P (20 Nm)\Butterfly valve linkage\
5490 | H6015X4-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 15 | 25 | 2500 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 300 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 15\
5232 | R417 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4520 |  |  | 309 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 20\
4996 | GR230A-5 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 150 s |  |  |  | AC 230 V | 40 Nm | IP54 | GR230A-5 | GR230A-5_datasheet_en-gb.pdf |  | PIC_EU_GR230A-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 318 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\GR..A (40 Nm)\Butterfly valve linkage\Open-Close, 3-point\AC 230 V\
276520 | DR24A-7 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 150 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DR24A-7 | DR24A-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 119 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
277661 | DRC24A-7 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DRC24A-7 | DRC24A-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 104 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\DRC..A (90 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
4995 | GR24A-5 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 150 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GR24A-5 | GR24A-5_datasheet_en-gb.pdf |  | PIC_EU_GR24A-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 326 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\GR..A (40 Nm)\Butterfly valve linkage\Open-Close, 3-point\AC/DC 24 V\
4999 | GR24A-SR-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 150 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GR24A-SR-5 | GR24A-SR-5_datasheet_en-gb.pdf |  | PIC_EU_GR24A-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 312 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\GR..A (40 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
61507 | DRC24G-T-7 | IP66/Nema4 actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 90 Nm | IP66 | DRC24G-T-7 | DRC24G-T-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24G-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦HH24-MG¦HT24-MG |  |  |  | 328 | EU\Products\Water solutions\Rotary product range actuators\IP66/NEMA4 actuator\DRC..G\Butterfly valve linkage\Open-Close\AC/DC 24 V\
5233 | R418 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4520 |  |  | 311 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 20\
276522 | DR24A-SR-7 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 150 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DR24A-SR-7 | DR24A-SR-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 135 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
5491 | H6020X4-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 20 | 25 | 2500 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 297 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 20\
61575 | D6500N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 500 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 24100 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S500 |  |  | 282 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
5492 | H6020X6P3-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 20 | 25 | 2500 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 304 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 20\
5495 | H6032X10-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 32 | 25 | 2500 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 293 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 32\
5494 | H6025X10-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 25 | 25 | 2500 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 302 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 25\
5234 | R419 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 8.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4520 |  |  | 309 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 20\
5493 | H6025X6P3-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 25 | 25 | 2500 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 298 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 25\
5228 | R411 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 311 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
277654 | GRC24G-5 | IP66/Nema4 actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 40 Nm | IP66 | GRC24G-5 | GRC24G-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24G-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦HH24-MG¦HT24-MG |  |  |  | 91 | EU\Products\Water solutions\Rotary product range actuators\IP66/NEMA4 actuator\DRC..G\Butterfly valve linkage\Open-Close\AC/DC 24 V\
5229 | R412 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 313 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
100026 | GRC24G-SZ-T-5 | IP66/Nema4 actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  | 35 s |  |  |  | AC/DC 24 V | 40 Nm | IP66 | GRC24G-SZ-T-5 | GRC24G-SZ-T-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24G-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦HH24-MG¦HT24-MG |  |  |  | 259 | EU\Products\Water solutions\Rotary product range actuators\IP66/NEMA4 actuator\DRC..G\Butterfly valve linkage\modulating\AC/DC 24 V\
99764 | ZD6N-S600 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S600 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 600 | [29 empty] | 177 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
5496 | H6032X16-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 32 | 25 | 2500 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 299 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 32\
5230 | R413 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 312 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
61576 | D6600N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 600 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 37300 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S600 |  |  | 285 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
61508 | DRC24A-TP-7 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DRC24A-TP-7 | DRC24A-TP-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24A-TP-7_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 309 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\DRC..A (90 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
5001 | GR24A-MF-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GR24A-MF-5 | GR24A-MF-5_datasheet_en-gb.pdf |  | PIC_EU_GR24A-MF-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN |  |  |  | 301 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\GR..A (40 Nm)\Butterfly valve linkage\modulating, MF\AC/DC 24 V\
61574 | D6450N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 450 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 18800 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S450 |  |  | 279 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
99765 | ZD6N-S700 | Butterfly valve |  | Actuator |  | Manual | [10 empty] | ZD6N-S700 |  |  | PIC_EU_ZD6N-S_Worm gear_BW.jpg | 700 | [29 empty] | 178 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
100394 | SR230P-5 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC 230 V | 20 Nm | IP66 + IP67 | SR230P-5 | SR230P-5_datasheet_en-gb.pdf |  | PIC_EU_Robustline-Water_1cab_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 271 | EU\Products\Water solutions\Rotary product range actuators\RobustLine actuators\SR..P (20 Nm)\Butterfly valve linkage\Open-Close, 3-point\AC 230 V\
61573 | D6400N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 400 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 14200 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S400 |  |  | 282 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
61577 | D6700N | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..N | D6..N_datasheet_en-gb.pdf |  | PIC_EU_D6..N_black_4C.jpg | 700 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 42800 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S700 |  |  | 277 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Wafer type, 2-way, PN16\D6..N\
5231 | R414 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 312 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 15\
5041 | NRF230A | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 230 V | 10 Nm | IP54 | NRF230A | NRF230A_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 324 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 230 V\
100395 | SR24P-5 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP66 + IP67 | SR24P-5 | SR24P-5_datasheet_en-gb.pdf |  | PIC_EU_Robustline-Water_1cab_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 235 | EU\Products\Water solutions\Rotary product range actuators\RobustLine actuators\SR..P (20 Nm)\Butterfly valve linkage\Open-Close, 3-point\AC/DC 24 V\
5042 | NRF230A-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 230 V | 10 Nm | IP54 | NRF230A-O | NRF230A-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 329 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 230 V\
5503 | H6100X125-SP2 | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..X..-SP2 | H6..X..-SP2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 100 | 25 | 2500 kPa |  |  |  | 125 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 298 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 100\
5236 | R423 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4525 |  |  | 310 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 25\
5500 | H6050X40-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 50 | 25 | 2500 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 299 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 50\
61578 | D6400NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 400 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 14200 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S400 |  |  | 279 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
61582 | D6700NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 700 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 42800 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S700 |  |  | 271 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5038 | NRF24A-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRF24A-O | NRF24A-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 317 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5501 | H6065X58-SP2 | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..X..-SP2 | H6..X..-SP2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 65 | 25 | 2500 kPa |  |  |  | 58 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 293 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 65\
5043 | NRF230A-S2 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC 230 V | 10 Nm | IP54 | NRF230A-S2 | NRF230A-S2_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 328 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 230 V\
277764 | CQ24A-SR-T | Rotary actuator (ZoneTight) | QCV | Actuator |  | modulating | DC 2...10 V |  |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A-SR-T | CQ24A-SR-T_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-SZ-T_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 100 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
61579 | D6450NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 450 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 18800 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S450 |  |  | 279 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5237 | R424 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4525 |  |  | 310 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 25\
5498 | H6040X25-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 40 | 25 | 2500 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 294 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 40\
281043 | C215QP-B | Pressure-independent zone valve | PIQCV | Valve | 2...90°C | [11 empty] | C2..QP-.. | C2..QP-.._datasheet_en-gb.pdf |  | PIC_EU_C2..QP-..4C.jpg | 15 | 25 | 1600 kPa | 700 kPa | 16 kPa | 350 kPa | [9 empty] | 210 l/h | 20 l/h | 30 l/h | 40 l/h |  | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread | 0 | Water | Pressure independent |  | ZR2315¦ZCQ-E¦ZCQ-FL |  |  | 146 | EU\Products\Water solutions\Rotary product range valves\Pressure-independent CCV\PIQCV\DN 15\
277763 | CQ24A-SR | Rotary actuator (ZoneTight) | QCV | Actuator |  | modulating | DC 2...10 V |  |  | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQ24A-SR | CQ24A-SR_datasheet_en-gb.pdf |  | PIC_EU_CQ24A-SZ_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 103 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
277682 | GRC24A-5 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GRC24A-5 | GRC24A-5_datasheet_en-gb.pdf |  | PIC_EU_GR24A-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 80 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\GRC..A (40 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
5238 | R429 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4532 |  |  | 304 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 25\
100453 | P6125W3100E-MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | P6..W..E-MP | P6..W..E-MP_datasheet_en-gb.pdf |  | PIC_EU_EPIV-schwarz_4C.jpg | 125 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 175 m³/h |  | 31 l/s | 1860 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | ZR24-F05¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 377 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
100450 | P6065W800E-MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | P6..W..E-MP | P6..W..E-MP_datasheet_en-gb.pdf |  | PIC_EU_EPIV-schwarz_4C.jpg | 65 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 45 m³/h |  | 8 l/s | 480 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | ZR24-F05¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 426 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
100465 | R3020-P63-1P6-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.63 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 267 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
61580 | D6500NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 500 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 24100 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S500 |  |  | 278 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5039 | NRF24A-S2 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 10 Nm | IP54 | NRF24A-S2 | NRF24A-S2_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 326 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5235 | R422 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4525 |  |  | 309 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 25\
100454 | P6150W4500E-MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | P6..W..E-MP | P6..W..E-MP_datasheet_en-gb.pdf |  | PIC_EU_EPIV-schwarz_4C.jpg | 150 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 270 m³/h |  | 45 l/s | 2700 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | ZR24-F05¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 384 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
100451 | P6080W1100E-MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | P6..W..E-MP | P6..W..E-MP_datasheet_en-gb.pdf |  | PIC_EU_EPIV-schwarz_4C.jpg | 80 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 65 m³/h |  | 11 l/s | 660 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | ZR24-F05¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 394 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
61581 | D6600NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 600 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 37300 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S600 |  |  | 282 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5239 | R431 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4532 |  |  | 307 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 32\
5044 | NRF230A-S2-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC 230 V | 10 Nm | IP54 | NRF230A-S2-O | NRF230A-S2-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 320 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 230 V\
277715 | DR24A-MP-7 | Rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  | 150 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DR24A-MP-7 | DR24A-MP-7_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 150 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\modulating, MP\AC/DC 24 V\
61589 | GRK24A-5 | SuperCap rotary actuator |  | Actuator |  | Open-close |  |  | NC / NO | 150 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GRK24A-5 | GRK24A-5_datasheet_en-gb.pdf |  | PIC_EU_GRKA_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 314 | EU\Products\Water solutions\Rotary product range actuators\SuperCap actuators\GRK..A\Open-Close\AC/DC 24 V\
5040 | NRF24A-S2-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 10 Nm | IP54 | NRF24A-S2-O | NRF24A-S2-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 326 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5502 | H6080X90-SP2 | Globe valve (partial pressure-balanced) | H | Valve | 5...150°C | [11 empty] | H6..X..-SP2 | H6..X..-SP2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 80 | 25 | 2500 kPa |  |  |  | 90 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 297 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 80\
5499 | H6050X25-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 50 | 25 | 2500 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 295 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 50\
5240 | R438 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4540 |  |  | 310 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 40\
100452 | P6100W2000E-MP | Communicative characterised control valve with sensor-operated flow control | EPIV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | P6..W..E-MP | P6..W..E-MP_datasheet_en-gb.pdf |  | PIC_EU_EPIV-schwarz_4C.jpg | 100 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 115 m³/h |  | 20 l/s | 1200 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | ZR24-F05¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 387 | EU\Products\Water solutions\VA Units\EPIV\modulating, MP\
5061 | NRQ24A | Very fast running rotary actuator |  | Actuator |  | Open-close |  |  |  | 9 s |  |  |  | AC/DC 24 V | 8 Nm | IP54 | NRQ24A | NRQ24A_datasheet_en-gb.pdf |  | PIC_EU_NRQ24A-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 276 | EU\Products\Water solutions\Rotary product range actuators\Very fast runner actuator\NRQ..A (8 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5514 | NR24A-MP | Rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NR24A-MP | NR24A-MP_datasheet_en-gb.pdf |  | PIC_EU_NR24A-MF-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 362 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\modulating, MP\AC/DC 24 V\
5073 | TRC24A-SR | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 15 s |  |  |  | AC/DC 24 V | 2 Nm | IP54 | TRC24A-SR | TRC24A-SR_datasheet_en-gb.pdf |  | PIC_EU_LR24A_SR_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 287 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\TRC..A (2 Nm)\Ball valve linkage\modulating\AC/DC 24 V\
5069 | LRQ24A | Very fast running rotary actuator |  | Actuator |  | Open-close |  |  |  | 9 s |  |  |  | AC/DC 24 V | 4 Nm | IP54 | LRQ24A | LRQ24A_datasheet_en-gb.pdf |  | PIC_EU_LRQ24A-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 303 | EU\Products\Water solutions\Rotary product range actuators\Very fast runner actuator\LRQ..A (4 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5542 | LRF24-MP | Spring-return rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus | NC | 75 s |  |  |  | AC/DC 24 V | 4 Nm | IP54 | LRF24-MP | LRF24-MP_datasheet_en-gb.pdf |  | PIC_EU_LRF24-MP_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP¦CR24-A3¦CR24-B3¦CRK24-B1 |  |  |  | 414 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\LRF.. (4 Nm)\Ball valve linkage\modulating, MP\AC/DC 24 V\
5245 | R506K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 298 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 10\
281044 | C215QP-D | Pressure-independent zone valve | PIQCV | Valve | 2...90°C | [11 empty] | C2..QP-.. | C2..QP-.._datasheet_en-gb.pdf |  | PIC_EU_C2..QP-..4C.jpg | 15 | 25 | 1600 kPa | 700 kPa | 16 kPa | 350 kPa | [9 empty] | 420 l/h | 50 l/h | 70 l/h | 100 l/h |  | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread |  | Water | Pressure independent |  | ZR2315¦ZCQ-E¦ZCQ-FL |  |  | 137 | EU\Products\Water solutions\Rotary product range valves\Pressure-independent CCV\PIQCV\DN 15\
281047 | C215QPT-B | Pressure-independent zone valve | PIQCV | Valve | 2...90°C | [11 empty] | C2..QPT-.. | C2..QPT-.._datasheet_en-gb.pdf |  | PIC_EU_C2..QPT-.._4C.jpg | 15 | 25 | 1600 kPa | 700 kPa | 16 kPa | 350 kPa | [9 empty] | 210 l/h | 20 l/h | 30 l/h | 40 l/h |  | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread | 1 | Water | Pressure independent |  | ZR2315¦ZCQ-E¦ZCQ-FL |  |  | 136 | EU\Products\Water solutions\Rotary product range valves\Pressure-independent CCV\PIQCV\DN 15\
5545 | SR24A-MP | Rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24A-MP | SR24A-MP_datasheet_en-gb.pdf |  | PIC_EU_SR24A-MP_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 375 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\modulating, MP\AC/DC 24 V\
100468 | R3020-1-2P5-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 2.5 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 263 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
100471 | R3020-1P6-1P6-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.6 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 261 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
5246 | R507K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 300 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 10\
100466 | R3020-P63-2P5-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.63 m³/h | 2.5 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 266 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
100467 | R3020-1-1P6-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 264 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
5546 | SR24A-MP-5 | Rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24A-MP-5 | SR24A-MP-5_datasheet_en-gb.pdf |  | PIC_EU_SR24A-MP-5-4c.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 375 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Butterfly valve linkage\modulating, MP\AC/DC 24 V\
5241 | R439 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4540 |  |  | 308 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 40\
5244 | R505K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 303 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 10\
281048 | C215QPT-D | Pressure-independent zone valve | PIQCV | Valve | 2...90°C | [11 empty] | C2..QPT-.. | C2..QPT-.._datasheet_en-gb.pdf |  | PIC_EU_C2..QPT-.._4C.jpg | 15 | 25 | 1600 kPa | 700 kPa | 16 kPa | 350 kPa | [9 empty] | 420 l/h | 50 l/h | 70 l/h | 100 l/h |  | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread | 1 | Water | Pressure independent |  | ZR2315¦ZCQ-E¦ZCQ-FL |  |  | 136 | EU\Products\Water solutions\Rotary product range valves\Pressure-independent CCV\PIQCV\DN 15\
5097 | H511B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515¦ZH515 |  |  | 306 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 15\
5242 | R448 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4550 |  |  | 310 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 50\
5541 | LR24A-MP | Rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | LR24A-MP | LR24A-MP_datasheet_en-gb.pdf |  | PIC_EU_LR24A-MP_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP¦CR24-A3¦CR24-B3¦CRK24-B1 |  |  |  | 326 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\modulating, MP\AC/DC 24 V\
100469 | R3020-1P6-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.6 m³/h | 0.63 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 265 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
61590 | GRK24A-SZ-5 | SuperCap rotary actuator |  | Actuator |  | modulating | DC 0.5...10 V |  | NC / NO | 150 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GRK24A-SZ-5 | GRK24A-SZ-5_datasheet_en-gb.pdf |  | PIC_EU_GRKA_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 305 | EU\Products\Water solutions\Rotary product range actuators\SuperCap actuators\GRK..A\modulating\AC/DC 24 V\
5071 | SR230A-5 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC 230 V | 20 Nm | IP54 | SR230A-5 | SR230A-5_datasheet_en-gb.pdf |  | PIC_EU_SR230A-5_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 346 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Butterfly valve linkage\Open-Close\AC 230 V\
5515 | TRF24-MFT | Spring-return rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus | NC | 90 s |  |  |  | AC/DC 24 V | 2.5 Nm | IP42 | TRF24-MFT | TRF24-MFT_datasheet_en-gb.pdf |  | PIC_EU_TRF-neutral_02_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 376 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\TRF.. (2.5 Nm)\Ball valve linkage\modulating, MF\AC/DC 24 V\
61600 | NRFA-S2 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC 24...240 V / DC 24...125 V | 10 Nm | IP54 | NRFA-S2 | NRFA-S2_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 304 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
281473 | C215Q-J | Zone valve | QCV | Valve | 2...90°C | [11 empty] | C2..Q-.. | C2..Q-.._datasheet_en-gb.pdf |  | PIC_EU_C2..Q-.._4C.jpg | 15 | 16 | 1600 kPa | 350 kPa |  | 280 kPa | 4.8 m³/h |  |  |  | 0.4 / 0.6 / 1 / 1.5 / 2 / 2.9 / 4 / 4.8 | [9 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread | 0 | Water | Control valve |  | ZR2315¦ZCQ-E |  |  | 124 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Zonen-Ventile\
5072 | SR24A-5 | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24A-5 | SR24A-5_datasheet_en-gb.pdf |  | PIC_EU_SR24A-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 357 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
5243 | R449 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R4..(K) | R4..(K)_datasheet_en-gb.pdf |  | PIC_EU_R4_neutral_01_2C.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 40 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | External thread |  | Water | Control valve | ZR24-2 | ZR4550 |  |  | 308 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 2-way\DN 50\
61598 | NRFA | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 24...240 V / DC 24...125 V | 10 Nm | IP54 | NRFA | NRFA_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 314 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
61596 | H6040X16-S2 | Globe valve | H | Valve | 5...150°C | [11 empty] | H6..X..-S2 | H6..X..-S2_datasheet_en-gb.pdf |  | PIC_EU_H6..X..-S(P)2-neutral_01_4C.jpg | 40 | 25 | 2500 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water¦Steam | Control valve |  |  |  |  | 268 | EU\Products\Water solutions\Globe valve range valves\PN25, flange\2-way\X\DN 40\
281045 | C220QP-F | Pressure-independent zone valve | PIQCV | Valve | 2...90°C | [11 empty] | C2..QP-.. | C2..QP-.._datasheet_en-gb.pdf |  | PIC_EU_C2..QP-..4C.jpg | 20 | 25 | 1600 kPa | 700 kPa | 16 kPa | 350 kPa | [9 empty] | 980 l/h | 90 l/h | 130 l/h | 190 l/h |  | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread | 0 | Water | Pressure independent |  | ZR2320¦ZCQ-E¦ZCQ-FL |  |  | 146 | EU\Products\Water solutions\Rotary product range valves\Pressure-independent CCV\PIQCV\DN 20\
100470 | R3020-1P6-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.6 m³/h | 1 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 263 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
5247 | R508K | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 10 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4510 |  |  | 299 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 10\
61592 | H6200W630-S7 | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..W..S7 | H6..W..S7_datasheet_en-gb.pdf |  | PIC_EU_H6..W-S7-neutral_01_SW.jpg | 200 | 16 | 1600 kPa |  |  |  | 630 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve |  |  |  |  | 256 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\W\DN 200\
61599 | NRFA-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC 24...240 V / DC 24...125 V | 10 Nm | IP54 | NRFA-O | NRFA-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [30 empty] | 302 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
281046 | C220QPT-F | Pressure-independent zone valve | PIQCV | Valve | 2...90°C | [11 empty] | C2..QPT-.. | C2..QPT-.._datasheet_en-gb.pdf |  | PIC_EU_C2..QPT-.._4C.jpg | 20 | 25 | 1600 kPa | 700 kPa | 16 kPa | 350 kPa | [9 empty] | 980 l/h | 90 l/h | 130 l/h | 190 l/h |  | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread | 1 | Water | Pressure independent |  | ZR2320¦ZCQ-E¦ZCQ-FL |  |  | 144 | EU\Products\Water solutions\Rotary product range valves\Pressure-independent CCV\PIQCV\DN 20\
5591 | SR24ALON | Rotary actuator |  | Actuator |  | communicative |  | LON (FTT-10A) |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SR24ALON | SR24ALON_datasheet_en-gb.pdf |  | PIC_EU_SR24ALON-neutral_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 331 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\SR..A (20 Nm)\Ball valve linkage\modulating, LON\AC/DC 24 V\
61593 | H6250W1000-S7 | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..W..S7 | H6..W..S7_datasheet_en-gb.pdf |  | PIC_EU_H6..W-S7-neutral_01_SW.jpg | 250 | 16 | 1600 kPa |  |  |  | 1000 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve |  |  |  |  | 258 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\W\DN 250\
5593 | NR24ALON | Rotary actuator |  | Actuator |  | communicative |  | LON (FTT-10A) |  | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NR24ALON | NR24ALON_datasheet_en-gb.pdf |  | PIC_EU_NR24A-MF-neutral_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 323 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\NR..A (10 Nm)\Ball valve linkage\modulating, LON\AC/DC 24 V\
5098 | H512B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515¦ZH515 |  |  | 282 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 15\
5100 | H514B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515¦ZH515 |  |  | 286 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 15\
5253 | R517 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4520 |  |  | 299 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 20\
5101 | H515B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515¦ZH515 |  |  | 283 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 15\
5252 | R513 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 302 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 15\
282466 | C315Q-H | Change-over zone valve | QCV | Valve | 2...90°C | [11 empty] | C3..Q-.. | C3..Q-.._datasheet_en-gb.pdf |  | PIC_EU_C3..Q-.._4C.jpg | 15 | 16 | 1600 kPa | 350 kPa |  | 280 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, tight (EN 12266-1) | 3-way | Internal thread | 0 | Water | Change-over valve |  | ZR2315¦ZCQ-E |  |  | 114 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Zonen-Ventile\
100476 | R3020-2P5-2P5-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 2.5 m³/h | 2.5 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 267 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
5622 | GR24A-MP-5 | Rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 | GR24A-MP-5 | GR24A-MP-5_datasheet_en-gb.pdf |  | PIC_EU_GR24A-MF-5_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 351 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\GR..A (40 Nm)\Butterfly valve linkage\modulating, MP\AC/DC 24 V\
100472 | R3020-1P6-2P5-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1.6 m³/h | 2.5 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 263 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
282431 | C220Q-K | Zone valve | QCV | Valve | 2...90°C | [11 empty] | C2..Q-.. | C2..Q-.._datasheet_en-gb.pdf |  | PIC_EU_C2..Q-.._4C.jpg | 20 | 16 | 1600 kPa | 350 kPa |  | 280 kPa | 8 m³/h |  |  |  | 0.5 / 0.8 / 1.3 / 1.9 / 2.8 / 4 / 5.7 / 8 | [9 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Internal thread | 0 | Water | Control valve |  | ZR2320¦ZCQ-E |  |  | 106 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Zonen-Ventile\
5103 | H525B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 25 | 16 | 1600 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4525¦ZH525 |  |  | 286 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 25\
61608 | R2015-P25-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 0.25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 331 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
5626 | SY5-24-MF-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 2...10 V |  |  | 30 s |  |  | 2 x SPDT | AC/DC 24 V | 500 Nm | IP67 | SY5-24-MF-T | SY5-24-MF-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [26 empty] | ZK2-GEN¦ZK6-GEN |  |  |  | 345 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY5.. (500 Nm)\modulating, MF\AC/DC 24 V\
5251 | R512 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 303 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 15\
5248 | R509 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 302 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 15\
5625 | SY4-24-MF-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 2...10 V |  |  | 23 s |  |  | 2 x SPDT | AC/DC 24 V | 400 Nm | IP67 | SY4-24-MF-T | SY4-24-MF-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [26 empty] | ZK2-GEN¦ZK6-GEN |  |  |  | 347 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY4.. (400 Nm)\modulating, MF\AC/DC 24 V\
283862 | ZCQ-FL | Butterfly valve |  | Actuator | [12 empty] | ZCQ-FL |  |  | PIC_EU_ZCQ-FL_4C.jpg | [30 empty] | 66 | EU\Products\Water solutions\Rotary product range actuators\Manual actuators\
100474 | R3020-2P5-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 2.5 m³/h | 1 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 265 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
5250 | R511 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 303 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 15\
100473 | R3020-2P5-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 2.5 m³/h | 0.63 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 261 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
61602 | NRFA-S2-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  | 2 x SPDT | AC 24...240 V / DC 24...125 V | 10 Nm | IP54 | NRFA-S2-O | NRFA-S2-O_datasheet_en-gb.pdf |  | PIC_EU_NRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 301 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\Open-Close\AC 24...240V / DC 24...125V\
100560 | SR230P-SR-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 90 s |  |  |  | AC 230 V | 20 Nm | IP66 + IP67 | SR230P-SR-5 | SR230P-SR-5_datasheet_en-gb.pdf |  | PIC_EU_Robustline-Water_2cab_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 269 | EU\Products\Water solutions\Rotary product range actuators\RobustLine actuators\SR..P (20 Nm)\Butterfly valve linkage\modulating\AC 230 V\
61609 | R2015-P4-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 0.4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 323 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
5102 | H520B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 20 | 16 | 1600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4520¦ZH520 |  |  | 285 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 20\
61604 | NVFT24-MFT-E | Spring-return globe valve actuator (TÜV) |  | Actuator |  | modulating | DC 2...10 V |  | NC |  | 150 s @ 15 / 18 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVFT24-MFT-E | H6..S+NVFT24-MFT-E_datasheet_en-gb.pdf |  | PIC_EU_NV-1K-neutral_01_4C.jpg | [26 empty] | ZK2-GEN |  |  |  | 289 | EU\Products\Water solutions\Globe valve range actuators\Spring return actuators\NVFT.. (1000N)\Standard\modulating, MFT\AC/DC 24 V\
5599 | NRF24A-MP | Spring-return rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus | NC | 90 s |  |  |  | AC/DC 24 V | 10 Nm | IP54 | NRF24A-MP | NRF24A-MP_datasheet_en-gb.pdf |  | PIC_EU_NRF-neutral-1K_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 408 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\NRF..A (10Nm/5Nm)\Ball valve linkage\modulating, MP\AC/DC 24 V\
5592 | LR24ALON | Rotary actuator |  | Actuator |  | communicative |  | LON (FTT-10A) |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | LR24ALON | LR24ALON_datasheet_en-gb.pdf |  | PIC_EU_LR24ALON_01_4C.jpg | [26 empty] | ZK1-GEN¦ZK2-GEN |  |  |  | 304 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\LR..A (5 Nm)\Ball valve linkage\modulating, LON\AC/DC 24 V\
283544 | CQK24A-SR | SuperCap rotary actuator (ZoneTight) |  | Actuator |  | modulating | DC 2...10 V |  | NC | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQK24A-SR | CQK24A-SR_datasheet_en-gb.pdf |  | PIC_EU_CQK24A-SZ._4C.jpg | [27 empty] | ZCQ-E |  |  | 93 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
5099 | H513B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515¦ZH515 |  |  | 287 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 15\
61610 | R2015-P63-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 330 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
282468 | C320Q-J | Change-over zone valve | QCV | Valve | 2...90°C | [11 empty] | C3..Q-.. | C3..Q-.._datasheet_en-gb.pdf |  | PIC_EU_C3..Q-.._4C.jpg | 20 | 16 | 1600 kPa | 350 kPa |  | 280 kPa | 4 m³/h | [13 empty] | Leakage rate A, tight (EN 12266-1) | 3-way | Internal thread | 0 | Water | Change-over valve |  | ZR2320¦ZCQ-E |  |  | 112 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Zonen-Ventile\
61611 | R2015-1-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 322 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
100903 | P6065W800EV-BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | P6..W..EV-BAC | P6..W..EV-BAC_datasheet_en-gb.pdf |  | PIC_EU_EnergyValve_black_4C.jpg | 65 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 40 m³/h |  | 8 l/s | 480 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | Z-STRJ.1¦ZR24-F05¦ZK1-GEN |  |  |  | 447 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
5249 | R510 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4515 |  |  | 301 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 15\
100475 | R3020-2P5-1P6-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 2.5 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 267 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
286571 | DRC24G-5 | IP66/Nema4 actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 90 Nm | IP66 | DRC24G-5 | DRC24G-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24G-neutral_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦HH24-MG¦HT24-MG |  |  |  | 64 | EU\Products\Water solutions\Rotary product range actuators\IP66/NEMA4 actuator\DRC..G\Butterfly valve linkage\Open-Close\AC/DC 24 V\
286575 | DR24A-MP-5 | Rotary actuator |  | Actuator |  | modulating¦communicative | DC 2...10 V | MP-Bus |  | 150 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DR24A-MP-5 | DR24A-MP-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A¦ZK1-GEN¦ZK2-GEN¦ZFP2-MP¦ZN230-24MP |  |  |  | 71 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\modulating, MP\AC/DC 24 V\
5633 | SY4-230-MF-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 2...10 V |  |  | 16 s |  |  | 2 x SPDT | AC 230 V | 400 Nm | IP67 | SY4-230-MF-T | SY4-230-MF-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [26 empty] | ZK6-GEN |  |  |  | 329 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY4.. (400 Nm)\modulating, MF\AC 230 V\
5634 | SY5-230-MF-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 2...10 V |  |  | 22 s |  |  | 2 x SPDT | AC 230 V | 500 Nm | IP67 | SY5-230-MF-T | SY5-230-MF-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [26 empty] | ZK6-GEN |  |  |  | 326 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY5.. (500 Nm)\modulating, MF\AC 230 V\
5258 | R531 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4532 |  |  | 298 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 32\
5254 | R518 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4520 |  |  | 298 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 20\
61619 | R2020-4-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2320 |  |  | 305 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 20\
286572 | DRC24A-5 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 35 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DRC24A-5 | DRC24A-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 65 | EU\Products\Water solutions\Rotary product range actuators\Fast runner actuators\DRC..A (90 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
5635 | SY6-230-MF-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 2...10 V |  |  | 32 s |  |  | 2 x SPDT | AC 230 V | 650 Nm | IP67 | SY6-230-MF-T | SY6-230-MF-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [26 empty] | ZK6-GEN |  |  |  | 348 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY6.. (750 Nm)\modulating, MF\AC 230 V\
61620 | R2020-6P3-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2320 |  |  | 310 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 20\
61614 | R2015-1P6-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 328 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
5257 | R529 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4532 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 32\
5109 | H413B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515 |  |  | 293 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 15\
100904 | P6080W1100EV-BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | P6..W..EV-BAC | P6..W..EV-BAC_datasheet_en-gb.pdf |  | PIC_EU_EnergyValve_black_4C.jpg | 80 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 60 m³/h |  | 11 l/s | 660 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | Z-STRJ.1¦ZR24-F05¦ZK1-GEN |  |  |  | 380 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
5108 | H412B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515 |  |  | 295 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 15\
5645 | SY5-230-SR-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 0.5...10 V |  |  | 22 s |  |  | 2 x SPDT | AC 230 V | 500 Nm | IP67 | SY5-230-SR-T | SY5-230-SR-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 307 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY5.. (500 Nm)\modulating\AC 230 V\
5104 | H532B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 32 | 16 | 1600 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4532¦ZH532 |  |  | 283 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 32\
100905 | P6100W2000EV-BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | P6..W..EV-BAC | P6..W..EV-BAC_datasheet_en-gb.pdf |  | PIC_EU_EnergyValve_black_4C.jpg | 100 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 100 m³/h |  | 20 l/s | 1200 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | Z-STRJ.1¦ZR24-F05¦ZK1-GEN |  |  |  | 386 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
61615 | R2015-2P5-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 314 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
100908 | LV24A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 15 mm | 500 N |  | AC/DC 24 V |  | IP54 | LV24A-TPC | LV24A-TPC_datasheet_en-gb.pdf |  | PIC_EU_LV24A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 283 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\LV..A (500N)\Open-Close, 3-point\AC/DC 24 V\
5259 | R538 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4540 |  |  | 300 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 40\
5629 | SY4-24-SR-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 0.5...10 V |  |  | 23 s |  |  | 2 x SPDT | AC/DC 24 V | 400 Nm | IP67 | SY4-24-SR-T | SY4-24-SR-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 304 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY4.. (400 Nm)\modulating\AC/DC 24 V\
5260 | R548 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 50 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4550 |  |  | 297 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 50\
286574 | DR24A-SR-5 | Rotary actuator |  | Actuator |  | modulating | DC 2...10 V |  |  | 150 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DR24A-SR-5 | DR24A-SR-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 66 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\modulating\AC/DC 24 V\
100906 | P6125W3100EV-BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | P6..W..EV-BAC | P6..W..EV-BAC_datasheet_en-gb.pdf |  | PIC_EU_EnergyValve_black_4C.jpg | 125 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 160 m³/h |  | 31 l/s | 1860 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | Z-STRJ.1¦ZR24-F05¦ZK1-GEN |  |  |  | 376 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
5644 | SY4-230-SR-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 0.5...10 V |  |  | 16 s |  |  | 2 x SPDT | AC 230 V | 400 Nm | IP67 | SY4-230-SR-T | SY4-230-SR-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 314 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY4.. (400 Nm)\modulating\AC 230 V\
5255 | R522 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4525 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 25\
61616 | R2015-4-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 314 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
100907 | P6150W4500EV-BAC | Characterised control valve with sensor-operated flow rate or power control, power and energy-monitoring function | EV | VA-Unit | -10...120°C | modulating¦communicative | DC 2...10 V | MP-Bus¦BACnet MS/TP¦BACnet IP |  | 90 s |  |  |  | AC/DC 24 V | 40 Nm | IP54 (for use of protective cap or grommet for RJ45 socket) | P6..W..EV-BAC | P6..W..EV-BAC_datasheet_en-gb.pdf |  | PIC_EU_EnergyValve_black_4C.jpg | 150 | 16 | 1600 kPa | 690 kPa |  | 340 kPa | [5 empty] | 240 m³/h |  | 45 l/s | 2700 l/min | [5 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Flange |  | Water | Pressure independent | Z-STRJ.1¦ZR24-F05¦ZK1-GEN |  |  |  | 382 | EU\Products\Water solutions\VA Units\EV\modulating, BAC\
101175 | LV230A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 15 mm | 500 N |  | AC 230 V |  | IP54 | LV230A-TPC | LV230A-TPC_datasheet_en-gb.pdf |  | PIC_EU_LV230A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 299 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\LV..A (500N)\Open-Close, 3-point\AC 230 V\
61617 | R2015-6P3-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 319 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 15\
5105 | H540B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 40 | 16 | 1600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4540¦ZH540 |  |  | 289 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 40\
5256 | R523 | Characterised control valve | CCV | Valve | 6...100°C | [11 empty] | R5..(K) | R5..(K)_datasheet_en-gb.pdf |  | PIC_EU_R5_neutral_01_2C.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 200 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | External thread |  | Water | Control valve | ZR24-2 | ZR4525 |  |  | 297 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\External thread, 3-way\DN 25\
286573 | DR230A-5 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 150 s |  |  |  | AC 230 V | 90 Nm | IP54 | DR230A-5 | DR230A-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 67 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\Open-Close\AC 230 V\
5630 | SY5-24-SR-T | Rotary actuator for butterfly valves |  | Actuator |  | modulating | DC 0.5...10 V |  |  | 30 s |  |  | 2 x SPDT | AC/DC 24 V | 500 Nm | IP67 | SY5-24-SR-T | SY5-24-SR-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 296 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY5.. (500 Nm)\modulating\AC/DC 24 V\
5107 | H411B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515 |  |  | 302 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 15\
61618 | R2015-S1 | Open-close ball valve | CV | Valve | -10...120°C | [11 empty] | R2..-S.. | R2..-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 15 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Shutt-off valve |  | ZR2315 |  |  | 309 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Internal thread, 2-way\DN 15\
5106 | H550B | Globe valve | H | Valve | 5...120°C | [11 empty] | H5..B | H5..B_datasheet_en-gb.pdf |  | PIC_EU_H5-B-neutral_01_4C.jpg | 50 | 16 | 1600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 3-way | External thread |  | Water | Control valve | ZH24-1 | ZH4550¦ZH550 |  |  | 284 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\3-way\B\DN 50\
5114 | H432B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 32 | 16 | 1600 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4532 |  |  | 291 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 32\
5110 | H414B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515 |  |  | 297 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 15\
5111 | H415B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4515 |  |  | 294 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 15\
61623 | R2025-6P3-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2325 |  |  | 316 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 25\
61624 | R2025-10-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2325 |  |  | 315 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 25\
61628 | R2032-16-S3 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2332 |  |  | 308 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 32\
5265 | D6125NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 125 | 10 / 16 | 1600 kPa |  |  | 4 kPa |  |  |  | 820 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150¦ZD6N-H150 |  |  | 291 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
286671 | R3020-4-2P5-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 4 m³/h | 2.5 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 64 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
286576 | DR24A-5 | Rotary actuator |  | Actuator |  | Open-close |  |  |  | 150 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DR24A-5 | DR24A-5_datasheet_en-gb.pdf |  | PIC_EU_DRC24A_01_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 68 | EU\Products\Water solutions\Rotary product range actuators\Standard actuators\CM..D.. (2 Nm)\Butterfly valve linkage\Open-Close\AC/DC 24 V\
5660 | SY9-230A-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 68 s |  |  | 2 x SPDT | AC 230 V | 2000 Nm | IP67 | SY9-230A-3-T | SY9-230A-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY9-SY12_4C.jpg | [30 empty] | 297 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY9.. (2000 Nm)\Open-Close\AC 230 V\
5657 | SY6-230-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 38 s |  |  | 2 x SPDT | AC 230 V | 650 Nm | IP67 | SY6-230-3-T | SY6-230-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 301 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY6.. (750 Nm)\Open-Close\AC 230 V\
5659 | SY8-230A-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 59 s |  |  | 2 x SPDT | AC 230 V | 1500 Nm | IP67 | SY8-230A-3-T | SY8-230A-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY7-SY8_4C.jpg | [30 empty] | 300 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY8.. (1500 Nm)\Open-Close\AC 230 V\
5261 | D650NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 50 | 10 / 16 | 1600 kPa |  |  | 10 kPa |  |  |  | 90 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 297 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5262 | D665NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 65 | 10 / 16 | 1600 kPa |  |  | 7 kPa |  |  |  | 180 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 295 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
101177 | NV24A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NV24A-TPC | NV24A-TPC_datasheet_en-gb.pdf |  | PIC_EU_NV24A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 299 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\NV..A (1000N)\Open-Close, 3-point\AC/DC 24 V\
286672 | R3020-4-4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 4 m³/h | 4 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 68 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
61625 | R2025-16-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2325 |  |  | 311 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 25\
101181 | SV24A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 20 mm | 1500 N |  | AC/DC 24 V |  | IP54 | SV24A-TPC | SV24A-TPC_datasheet_en-gb.pdf |  | PIC_EU_SV24A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 272 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\SV..A (1500N)\Open-Close, 3-point\AC/DC 24 V\
5115 | H440B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 40 | 16 | 1600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4540 |  |  | 295 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 40\
5266 | D6150NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 150 | 10 / 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 1600 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150¦ZD6N-H150 |  |  | 289 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5112 | H420B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 20 | 16 | 1600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4520 |  |  | 294 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 20\
5263 | D680NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 80 | 10 / 16 | 1600 kPa |  |  | 6 kPa |  |  |  | 300 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 293 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
101187 | EV230A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 40 mm | 2500 N |  | AC 230 V |  | IP54 | EV230A-TPC | EV230A-TPC_datasheet_en-gb.pdf |  | PIC_EU_EV230A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 316 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\EV..A (2500N)\Open-Close, 3-point\AC 230 V\
61622 | R2020-S2 | Open-close ball valve | CV | Valve | -10...120°C | [11 empty] | R2..-S.. | R2..-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Shutt-off valve |  | ZR2320 |  |  | 300 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Internal thread, 2-way\DN 20\
5658 | SY7-230A-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 58 s |  |  | 2 x SPDT | AC 230 V | 1000 Nm | IP67 | SY7-230A-3-T | SY7-230A-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY7-SY8_4C.jpg | [30 empty] | 303 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY7.. (1000 Nm)\Open-Close\AC 230 V\
286583 | DRK24A-5 | SuperCap rotary actuator |  | Actuator |  | Open-close |  |  | NC / NO | 150 s |  |  |  | AC/DC 24 V | 90 Nm | IP54 | DRK24A-5 | DRK24A-5_datasheet_en-gb.pdf |  | PIC_EU_DRK24A_4C.jpg | [26 empty] | S1A¦S2A¦P140A¦P200A¦P500A¦P1000A¦P2800A¦P5000A¦P10000A |  |  |  | 77 | EU\Products\Water solutions\Rotary product range actuators\SuperCap actuators\DRK..A\Open-Close\AC/DC 24 V\
287720 | CQK24A-SR-O | SuperCap rotary actuator (ZoneTight) |  | Actuator |  | modulating | DC 2...10 V |  | NO | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQK24A-SR-O | CQK24A-SR-O_datasheet_en-gb.pdf |  | PIC_EU_CQK24A-SZ._4C.jpg | [27 empty] | ZCQ-E |  |  | 59 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
5656 | SY5-230-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 29 s |  |  | 2 x SPDT | AC 230 V | 500 Nm | IP67 | SY5-230-3-T | SY5-230-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 307 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY5.. (500 Nm)\Open-Close\AC 230 V\
5116 | H450B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 50 | 16 | 1600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4550 |  |  | 293 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 50\
5113 | H425B | Globe valve | H | Valve | 5...120°C | [11 empty] | H4..B | H4..B_datasheet_en-gb.pdf |  | PIC_EU_H4-B-neutral_01_4C.jpg | 25 | 16 | 1600 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | External thread |  | Water | Control valve | ZH24-1 | ZH4525 |  |  | 298 | EU\Products\Water solutions\Globe valve range valves\PN16, external thread\2-way\B\DN 25\
5655 | SY4-230-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 21 s |  |  | 2 x SPDT | AC 230 V | 400 Nm | IP67 | SY4-230-3-T | SY4-230-3-T_datasheet_de-ch.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 316 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY4.. (400 Nm)\Open-Close\AC 230 V\
61627 | R2025-S2 | Open-close ball valve | CV | Valve | -10...120°C | [11 empty] | R2..-S.. | R2..-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 26 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Shutt-off valve |  | ZR2325 |  |  | 298 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Internal thread, 2-way\DN 25\
101192 | NVK24A-3-TPC | SuperCap globe valve actuator |  | Actuator |  | 3-point |  |  | NC / NO |  | 150 s / 20 mm | 1000 N |  | AC 24 V |  | IP54 | NVK24A-3-TPC | NVK24A-3-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVK24A-3-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 335 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVK..A (1000N)\Open-Close, 3-point\AC/DC 24 V\
101183 | SV230A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 20 mm | 1500 N |  | AC 230 V |  | IP54 | SV230A-TPC | SV230A-TPC_datasheet_en-gb.pdf |  | PIC_EU_SV230A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 277 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\SV..A (1500N)\Open-Close, 3-point\AC 230 V\
101185 | EV24A-TPC | Globe valve actuator |  | Actuator |  | Open-close¦3-point |  |  |  |  | 150 s / 40 mm | 2500 N |  | AC/DC 24 V |  | IP54 | EV24A-TPC | EV24A-TPC_datasheet_en-gb.pdf |  | PIC_EU_EV24A-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 280 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\EV..A (2500N)\Open-Close, 3-point\AC/DC 24 V\
287721 | CQK24A | SuperCap rotary actuator (ZoneTight) |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQK24A | CQK24A_datasheet_en-gb.pdf |  | PIC_EU_CQK24A-SZ._4C.jpg | [27 empty] | ZCQ-E |  |  | 63 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
5264 | D6100NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 100 | 10 / 16 | 1600 kPa |  |  | 4 kPa |  |  |  | 580 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve | ZR24-F05 | ZD6N-S100¦ZD6N-H100 |  |  | 292 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
286668 | R3020-2P5-4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 2.5 m³/h | 4 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 70 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
287722 | CQK24A-O | SuperCap rotary actuator (ZoneTight) |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC/DC 24 V | 1 Nm | IP40 | CQK24A-O | CQK24A-O_datasheet_en-gb.pdf |  | PIC_EU_CQK24A-SZ._4C.jpg | [27 empty] | ZCQ-E |  |  | 60 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
101220 | LV24A-SR-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 150 s / 15 mm | 500 N |  | AC/DC 24 V |  | IP54 | LV24A-SR-TPC | LV24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_LV24A-SR..SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 278 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\LV..A (500N)\modulating\AC/DC 24 V\
101214 | NVK230A-3 | SuperCap globe valve actuator |  | Actuator |  | 3-point |  |  | NC / NO |  | 150 s / 20 mm | 1000 N |  | AC 230 V |  | IP54 | NVK230A-3 | NVK230A-3_datasheet_en-gb.pdf |  | PIC_EU_NVK230A-3_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 299 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\NVK..A (1000N)\Open-Close, 3-point\AC 230 V\
5663 | SY12-230A-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 74 s |  |  | 2 x SPDT | AC 230 V | 3500 Nm | IP67 | SY12-230A-3-T | SY12-230A-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY9-SY12_4C.jpg | [30 empty] | 301 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY12.. (3500 Nm)\Open-Close\AC 230 V\
61639 | R2040-S3 | Open-close ball valve | CV | Valve | -10...120°C | [11 empty] | R2..-S.. | R2..-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 31 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Shutt-off valve |  | ZR2340 |  |  | 293 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Internal thread, 2-way\DN 40\
5122 | H620N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 20 | 16 | 1600 kPa |  |  |  | 6.3 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 274 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 20\
61643 | R3015-P25-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 0.25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 330 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 15\
5279 | R3015-P25-P4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.25 m³/h | 0.4 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 350 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
61629 | R2032-S3 | Open-close ball valve | CV | Valve | -10...120°C | [11 empty] | R2..-S.. | R2..-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 32 | 16 | 1600 kPa | 1400 kPa |  | 1000 kPa | 32 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Shutt-off valve |  | ZR2332 |  |  | 291 | EU\Products\Water solutions\Rotary product range valves\Shut-off ball valves\Internal thread, 2-way\DN 32\
5118 | H612N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 273 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 15\
61637 | R2040-16-S3 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 16 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2340 |  |  | 306 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 40\
287983 | D6250WL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..WL | D6..WL_datasheet_en-gb.pdf |  | PIC_EU_D6..WL_4C.jpg | 250 | 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 4400 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150 |  |  | 83 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Drosselklappen\Lug-Type, 2-Weg\D6..WL\
287982 | D6250W | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..W | D6..W_datasheet_en-gb.pdf |  | PIC_EU_D6..W_4C.jpg | 250 | 6 / 10 / 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 4400 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150 |  |  | 82 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Drosselklappen\Wafer-Type, 2-Weg, PN16\D6..W\
287984 | D6300W | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..W | D6..W_datasheet_en-gb.pdf |  | PIC_EU_D6..W_4C.jpg | 300 | 6 / 10 / 16 | 1600 kPa |  |  | 2 kPa |  |  |  | 7300 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150 |  |  | 80 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Drosselklappen\Wafer-Type, 2-Weg, PN16\D6..W\
101216 | AVK24A-3-TPC | SuperCap globe valve actuator |  | Actuator |  | 3-point |  |  | NC / NO |  | 150 s / 32 mm | 2000 N |  | AC 24 V |  | IP54 | AVK24A-3-TPC | AVK24A-3-TPC_datasheet_en-gb.pdf |  | PIC_EU_AVK24A-3-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 325 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\AVK..A (2000N)\Open-Close, 3-point\AC/DC 24 V\
5661 | SY10-230A-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 73 s |  |  | 2 x SPDT | AC 230 V | 2500 Nm | IP67 | SY10-230A-3-T | SY10-230A-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY9-SY12_4C.jpg | [30 empty] | 301 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY10.. (2500 Nm)\Open-Close\AC 230 V\
5280 | R3015-P25-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.25 m³/h | 0.63 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 353 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5119 | H613N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 273 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 15\
101219 | LVC24A-SZ-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 35 s / 15 mm | 500 N |  | AC/DC 24 V |  | IP54 | LVC24A-SZ-TPC | LVC24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_LVC24A-SR..SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 260 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\LVC..A (500N)\modulating\AC/DC 24 V\
101221 | LVC24A-SR-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 35 s / 15 mm | 500 N |  | AC/DC 24 V |  | IP54 | LVC24A-SR-TPC | LVC24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_LVC24A-SR..SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 265 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\LVC..A (500N)\modulating\AC/DC 24 V\
287980 | D6200W | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..W | D6..W_datasheet_en-gb.pdf |  | PIC_EU_D6..W_4C.jpg | 200 | 6 / 10 / 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 2900 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150 |  |  | 80 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Drosselklappen\Wafer-Type, 2-Weg, PN16\D6..W\
61644 | R3015-P4-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 0.4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 327 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 15\
5120 | H614N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 276 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 15\
287981 | D6200WL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..WL | D6..WL_datasheet_en-gb.pdf |  | PIC_EU_D6..WL_4C.jpg | 200 | 16 | 1600 kPa |  |  | 2.5 kPa |  |  |  | 2900 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150 |  |  | 82 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Drosselklappen\Lug-Type, 2-Weg\D6..WL\
61645 | R3015-P63-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 0.63 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 328 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 15\
61638 | R2040-25-S3 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R2..xx-S.. | R2..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R2-neueCCV_01_SW.jpg | 40 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 25 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 2-way | Internal thread |  | Water | Control valve |  | ZR2340 |  |  | 306 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 2-way\DN 40\
5270 | D6350NL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..NL | D6..NL_datasheet_en-gb.pdf |  | PIC_EU_D6..NL_black_4C.jpg | 350 | 16 | 1600 kPa |  |  | 1.5 kPa |  |  |  | 10900 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S350 |  |  | 289 | EU\Products\Water solutions\Rotary product range valves\Butterfly valves\Lug type, 2-way\D6..NL\
5278 | R3015-P25-P25-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.25 m³/h | 0.25 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 375 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5281 | R3015-P25-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.25 m³/h | 1 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 359 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
101218 | LV24A-SZ-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 150 s / 15 mm | 500 N |  | AC/DC 24 V |  | IP54 | LV24A-SZ-TPC | LV24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_LV24A-SR..SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 287 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\LV..A (500N)\modulating\AC/DC 24 V\
5282 | R3015-P25-1P3-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.25 m³/h | 1.3 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 350 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
101217 | AVK230A-3 | SuperCap globe valve actuator |  | Actuator |  | 3-point |  |  | NC / NO |  | 150 s / 32 mm | 2000 N |  | AC 230 V |  | IP54 | AVK230A-3 | AVK230A-3_datasheet_en-gb.pdf |  | PIC_EU_AVK230A-3_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 329 | EU\Products\Water solutions\Globe valve range actuators\SuperCap actuators (incl. Fast runner)\AVK..A (2000N)\Open-Close, 3-point\AC 230 V\
5117 | H611N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 279 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 15\
5121 | H615N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 15 | 16 | 1600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 279 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 15\
59904 | SRF24A-O | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NO | 75 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A-O | SRF24A-O_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 308 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
101223 | NVC24A-SZ-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 35 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVC24A-SZ-TPC | NVC24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVC24A-SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 257 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\NVC..A (1000N)\modulating\AC/DC 24 V\
101226 | NV24A-SR-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NV24A-SR-TPC | NV24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_NV24A-SR..SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 286 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\NV..A (1000N)\modulating\AC/DC 24 V\
59905 | SRF24A-S2 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC/DC 24 V | 20 Nm | IP54 | SRF24A-S2 | SRF24A-S2_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 314 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
5127 | H664N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 65 | 16 | 1600 kPa |  |  |  | 58 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 272 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 65\
101227 | NVC24A-SR-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 35 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NVC24A-SR-TPC | NVC24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_NVC24A-SR-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 266 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\NVC..A (1000N)\modulating\AC/DC 24 V\
5283 | R3015-P4-P25-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.4 m³/h | 0.25 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 346 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
61648 | R3015-2P5-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 2.5 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 327 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 15\
5284 | R3015-P4-P4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.4 m³/h | 0.4 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 348 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
61650 | R3020-4-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2320 |  |  | 323 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 20\
5288 | R3015-P63-P25-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.63 m³/h | 0.25 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 351 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5285 | R3015-P4-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.4 m³/h | 0.63 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 349 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5289 | R3015-P63-P4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.63 m³/h | 0.4 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 347 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
61649 | R3015-4-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 4 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 334 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 15\
5124 | H632N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 32 | 16 | 1600 kPa |  |  |  | 16 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 275 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 32\
5123 | H625N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 25 | 16 | 1600 kPa |  |  |  | 10 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 273 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 25\
288687 | CQC230A | Rotary actuator (ZoneTight) | QCV | Actuator |  | Open-close¦3-point |  |  |  | 35 s |  |  |  | AC 230 V | 1 Nm | IP40 | CQC230A | CQC230A_datasheet_en-gb.pdf |  | PIC_EU_CQ24A_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 41 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
101228 | SV24A-SZ-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 150 s / 20 mm | 1500 N |  | AC/DC 24 V |  | IP54 | SV24A-SZ-TPC | SV24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_SV24A-SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 268 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\SV..A (1500N)\modulating\AC/DC 24 V\
288665 | PRCA-S2-T | Rotary actuator |  | Actuator |  | Open-close¦3-point |  |  |  | 35 s |  |  | 2 x SPDT | AC 24...240 V / DC 24...125 V | 160 Nm | IP66 + IP67 | PRCA-S2-T | PRCA-S2-T_datasheet_en-gb.pdf |  | PIC_EU_PR.._4C.jpg | [27 empty] | ZPR01¦ZPR02¦ZPR03¦ZPR05¦ZPR06¦ZPR08¦ZPR09¦ZPR10¦ZPR11¦ZPR12 |  |  | 182 | EU\Produkte\Wasseranwendungen\Drehsortiment Antriebe\Standardantriebe\PR.. (160 Nm)\Auf-Zu, 3-Punkt\
5286 | R3015-P4-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.4 m³/h | 1 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 350 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5129 | H679N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 80 | 16 | 1600 kPa |  |  |  | 90 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 274 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 80\
287985 | D6300WL | Butterfly valve | BFV | Valve | -20...120°C | [11 empty] | D6..WL | D6..WL_datasheet_en-gb.pdf |  | PIC_EU_D6..WL_4C.jpg | 300 | 16 | 1600 kPa |  |  | 2 kPa |  |  |  | 7300 m³/h | [10 empty] | Leakage rate A, tight (EN 12266-1) | 2-way | Flange |  | Water | Shutt-off valve |  | ZD6N-S150 |  |  | 83 | EU\Produkte\Wasseranwendungen\Drehsortiment Ventile\Drosselklappen\Lug-Type, 2-Weg\D6..WL\
5128 | H665N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 65 | 16 | 1600 kPa |  |  |  | 63 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 276 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 65\
288688 | CQD230A | Rotary actuator (ZoneTight) | QCV | Actuator |  | Open-close¦3-point |  |  |  | 15 s |  |  |  | AC 230 V | 1 Nm | IP40 | CQD230A | CQD230A_datasheet_en-gb.pdf |  | PIC_EU_CQ24A_4C.jpg | [27 empty] | ZCQ-E¦ZCQ-W |  |  | 40 | EU\Products\Water solutions\Rotary product range actuators\CQ actuator\
5125 | H640N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 40 | 16 | 1600 kPa |  |  |  | 25 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 273 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 40\
5287 | R3015-P4-1P3-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.4 m³/h | 1.3 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 348 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5126 | H650N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 50 | 16 | 1600 kPa |  |  |  | 40 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 275 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 50\
61647 | R3015-1P6-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 1.6 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 330 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 15\
101229 | SVC24A-SZ-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 35 s / 20 mm | 1500 N |  | AC/DC 24 V |  | IP54 | SVC24A-SZ-TPC | SVC24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_SVC24A-SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 256 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\SVC..A (1500N)\modulating\AC/DC 24 V\
59903 | SRF24A | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC/DC 24 V | 20 Nm | IP54 | SRF24A | SRF24A_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 304 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC/DC 24 V\
61646 | R3015-1-S1 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 15 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 1 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2315 |  |  | 327 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 15\
61652 | R3025-6P3-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2325 |  |  | 327 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 25\
101222 | NV24A-SZ-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 150 s / 20 mm | 1000 N |  | AC/DC 24 V |  | IP54 | NV24A-SZ-TPC | NV24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_LV24A-SR..SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 280 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\NV..A (1000N)\modulating\AC/DC 24 V\
61651 | R3020-6P3-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 20 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 6.3 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2320 |  |  | 318 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 20\
101230 | SV24A-SR-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 150 s / 20 mm | 1500 N |  | AC/DC 24 V |  | IP54 | SV24A-SR-TPC | SV24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_SV24A-SR-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 266 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\SV..A (1500N)\modulating\AC/DC 24 V\
101233 | EVC24A-SZ | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 35 s / 40 mm | 2500 N |  | AC/DC 24 V |  | IP54 | EVC24A-SZ | EVC24A-SZ_datasheet_en-gb.pdf |  | PIC_EU_EVC24A-SZ_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 254 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\EVC..A (2500N)\modulating\AC/DC 24 V\
59921 | SY4-24-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 30 s |  |  | 2 x SPDT | AC/DC 24 V | 400 Nm | IP67 | SY4-24-3-T | SY4-24-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 320 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY4.. (400 Nm)\Open-Close\AC 24 V\
5131 | H6100N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 100 | 16 | 1600 kPa |  |  |  | 145 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 272 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 100\
101234 | EV24A-SR-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 150 s / 40 mm | 2500 N |  | AC/DC 24 V |  | IP54 | EV24A-SR-TPC | EV24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_EV24A-SR-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 278 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\EV..A (2500N)\modulating\AC/DC 24 V\
59906 | SRF230A | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  |  | AC 230 V | 20 Nm | IP54 | SRF230A | SRF230A_datasheet_en-gb.pdf |  | PIC_EU_SRF-neutral-1K_01_4C.jpg | [30 empty] | 295 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 230 V\
305190 | R3020-4-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 |  |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 19 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
303851 | EP015R-R6+BAC | Characterised control valve with sensor-operated flow control | 6-way EPIV | VA-Unit | 6...80°C | modulating¦communicative | DC 2...10 V | Modbus RTU¦BACnet MS/TP¦MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | EP..R-R6+BAC |  |  | PIC_EU_EP..R-R6+BAC_4C.jpg | 15 | 16 | 1600 kPa |  |  | 110 kPa | [5 empty] | 1.2 m³/h |  |  |  | 1260 l/h |  |  |  | 840 l/h | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Pressure independent | CRK24-B1 | ZR2315¦ZR-004 | 1.05 l/min | 1.05 l/min | 54 | EU\Products\Water solutions\VA Units\EPIV\6-way EPIV\
5292 | R3015-P63-1P3-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.63 m³/h | 1.3 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 350 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5293 | R3015-1-P25-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 0.25 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 347 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
5134 | H613R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 1.6 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 284 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 15\
303852 | EP020R-R6+BAC | Characterised control valve with sensor-operated flow control | 6-way EPIV | VA-Unit | 6...80°C | modulating¦communicative | DC 2...10 V | Modbus RTU¦BACnet MS/TP¦MP-Bus |  | 90 s |  |  |  | AC/DC 24 V | 5 Nm | IP54 | EP..R-R6+BAC |  |  | PIC_EU_EP..R-R6+BAC_4C.jpg | 20 | 16 | 1600 kPa |  |  | 110 kPa | [5 empty] | 2.3 m³/h |  |  |  | 2340 l/h |  |  |  | 1620 l/h | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Pressure independent | CRK24-B1 | ZR2320¦ZR-004 | 1.95 l/min | 18.6 l/min | 47 | EU\Products\Water solutions\VA Units\EPIV\6-way EPIV\
5290 | R3015-P63-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.63 m³/h | 0.63 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 353 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
61653 | R3025-10-S2 | Characterised control valve | CCV | Valve | -10...120°C | [11 empty] | R3..xx-S.. | R3..xx-S.._datasheet_en-gb.pdf |  | PIC_EU_R3-neueCCV_01_SW.jpg | 25 | 16 | 1600 kPa | 1400 kPa |  | 350 kPa | 10 m³/h | [13 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 3-way | Internal thread |  | Water | Control valve |  | ZR2325 |  |  | 326 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 3-way\DN 25\
59922 | SY5-24-3-T | Rotary actuator for butterfly valves |  | Actuator |  | Open-close¦3-point |  |  |  | 35 s |  |  | 2 x SPDT | AC/DC 24 V | 500 Nm | IP67 | SY5-24-3-T | SY5-24-3-T_datasheet_en-gb.pdf |  | PIC_EU_SY2-SY6_4C.jpg | [30 empty] | 311 | EU\Products\Water solutions\Rotary product range actuators\SY actuators\SY5.. (500 Nm)\Open-Close\AC 24 V\
5130 | H680N | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..N | H6..N_datasheet_en-gb.pdf |  | PIC_EU_H625N_4C.jpg | 80 | 16 | 1600 kPa |  |  |  | 100 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1-C |  |  |  | 278 | EU\Products\Water solutions\Globe valve range valves\PN16, flange\2-way\N\DN 80\
101232 | EV24A-SZ-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 0.5...10 V |  |  |  | 150 s / 40 mm | 2500 N |  | AC/DC 24 V |  | IP54 | EV24A-SZ-TPC | EV24A-SZ-TPC_datasheet_en-gb.pdf |  | PIC_EU_EV24A-SZ-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 275 | EU\Products\Water solutions\Globe valve range actuators\Standard actuators\EV..A (2500N)\modulating\AC/DC 24 V\
101231 | SVC24A-SR-TPC | Globe valve actuator |  | Actuator |  | modulating | DC 2...10 V |  |  |  | 35 s / 20 mm | 1500 N |  | AC/DC 24 V |  | IP54 | SVC24A-SR-TPC | SVC24A-SR-TPC_datasheet_en-gb.pdf |  | PIC_EU_SVC24A-SR-TPC_01_4C.jpg | [26 empty] | S2A-H |  |  |  | 262 | EU\Products\Water solutions\Globe valve range actuators\Fast runner actuators\SVC..A (1500N)\modulating\AC/DC 24 V\
305191 | R3020-4-1P6-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 |  |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 21 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
305188 | R3020-1-4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 |  |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 19 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
5133 | H612R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 1 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 296 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 15\
5135 | H614R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 2.5 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 287 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 15\
5132 | H611R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 0.63 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 306 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 15\
305189 | R3020-1P6-4-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 |  |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 19 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\
5291 | R3015-P63-1-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 | R30..-..-..-B2_datasheet_en-gb.pdf |  | PIC_EU_R3015..-B2_02_4C.jpg | 15 | 16 | 1600 kPa |  |  | 100 kPa |  | 0.63 m³/h | 1 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2315 |  |  | 348 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 15\
59907 | SRF230A-S2 | Spring-return rotary actuator |  | Actuator |  | Open-close |  |  | NC | 75 s |  |  | 2 x SPDT | AC 230 V | 20 Nm | IP54 | SRF230A-S2 | SRF230A-S2_datasheet_en-gb.pdf |  | PIC_EU_SRF-S2-neutral-2K_01_4C.jpg | [30 empty] | 307 | EU\Products\Water solutions\Rotary product range actuators\Spring return actuators\SRF..A (20 Nm)\Ball valve linkage\Open-Close\AC 230 V\
5136 | H615R | Globe valve | H | Valve | 5...120°C | [11 empty] | H6..R | H6..R_datasheet_en-gb.pdf |  | PIC_EU_H625R_4C.jpg | 15 | 6 | 600 kPa |  |  |  | 4 m³/h | [13 empty] | max. 0.05% of the kvs value | 2-way | Flange |  | Water | Control valve | ZH24-1 |  |  |  | 284 | EU\Products\Water solutions\Globe valve range valves\PN6, flange\2-way\reduced\DN 15\
305192 | R3020-4-P63-B2 | Characterised control valve | 6-way CCV | Valve | 6...80°C | [11 empty] | R30..-..-..-B2 |  |  | PIC_EU_R3015..-B2_02_4C.jpg | 20 | 16 | 1600 kPa |  |  | 100 kPa |  | 1 m³/h | 1.6 m³/h | [11 empty] | Leakage rate A, air-bubble-tight (EN 12266-1) | 6-way | Internal thread |  | Water | Control valve |  | ZR-004¦ZR2320 |  |  | 19 | EU\Products\Water solutions\Rotary product range valves\Characterised control valves\Internal thread, 6-way\DN 20\